| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| MTO FOR POWER & CONTROL CABLES نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| D02 | Apr.2025 | IFI | E.Zamani | M.Fakharian | S.Faramarzpour |  |
| D01 | Dec. 2023 | IFI | H.Shakiba | M.Fakharian | S.Faramarzpour |  |
| D00 | May. 2023 | IFI | H.Shakiba | M.Fakharian | A.M.Mohseni |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:3 |  | Client Doc. Number: F8Z-709075 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X |  |  |  | 51 |  |  |  |  |  |
| 2 | X | X | X |  |  |  | 52 |  |  |  |  |  |
| 3 | X | X | X |  |  |  | 53 |  |  |  |  |  |
| 4 | X | X | X |  |  |  | 54 |  |  |  |  |  |
| 5 | X | X | X |  |  |  | 55 |  |  |  |  |  |
| 6 | X | X | X |  |  |  | 56 |  |  |  |  |  |
| 7 | X | X | X |  |  |  | 57 |  |  |  |  |  |
| 8 | X | X | X |  |  |  | 58 |  |  |  |  |  |
| 9 |  | X | X |  |  |  | 59 |  |  |  |  |  |
| 10 |  | X | X |  |  |  | 60 |  |  |  |  |  |
| 11 |  | X | X |  |  |  | 61 |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

D02

Electrical Cable Type

A : Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH)

B : Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE)

C : Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE)

D : Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH)

E : Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE)

F : Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH)

F1 : Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (HV MULTI-CORE WITH LEAD SHEATH)

G : Cu/SC/XLPE/SC/SCT/Lsh/Bd/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE WITH LEAD SHEATH)

H : Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE)

I : Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE)

J : CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE)

K : CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE)

L : Cu/PVC/PVC - NYY (LV MULTI-CORE FOR LIGHTING)

R : Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE)

S : CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE OR EPR or H07 RN-F)

Z : MICC FIRE RESISTANTCABLE( Mineral Insulated Copper Cable ) FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS … .

| 11 KV POWER CABLE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| D02 Insulation Grade - Service Voltage: 12/20 (24) KV |  |  |  |  |  |
| Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |
| Insulation: XLPE Insulation (Color Coding as per IEC) |  |  |  |  |  |
| Semiconducting Material: Yes |  |  |  |  |  |
| Screening : Semi-Conductor |  |  |  |  |  |
| Binder Tape: Yes |  |  |  |  |  |
| Fillers : PVC |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |
| Armor: Multi-Core Cables : Galvanized Steel Wire Armor (SWA) Single-Core Cables : Aluminum Wire Armor (AWA) |  |  |  |  |  |
| Other Sheath: PVC (UV Resistant & Flame Retardant with Red Color) |  |  |  |  |  |
| Color of Core: - 1Core Cables= Black - 3Cores Cables= Red, Yellow, Blue |  |  |  |  |  |
| Item | Description | Type | Quantity (m) | Spare (m) | Total (m) |
|  | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC |  |  |  |  |
|  | 3C×95 mm2 | I | 405 | 45 | 450 |
|  | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC |  |  |  |  |
|  | 3C×95 mm2 | F | 900 | 50 | 950 |
| Total Cable |  |  |  |  | 1350 |

| 3.3 KV POWER CABLE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulation Grade - Service Voltage: 6/10 (12) KV |  |  |  |  |  |
| D02 Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |
| Insulation: XLPE Insulation (Color coding as per IEC) |  |  |  |  |  |
| Semiconducting Material: Yes |  |  |  |  |  |
| Screening : Semi-Conductor |  |  |  |  |  |
| Binder Tape: Yes |  |  |  |  |  |
| Fillers : PVC (UV Resistant & Flame Retardant with Red Color) |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |
| Armor: Multi-Core Cables : Galvanized Steel Wire Armor (SWA) Single-Core Cables : Aluminum Wire Armor (AWA) |  |  |  |  |  |
| Other Sheath: PVC (UV Resistant & Flame Retardant with Red Color) |  |  |  |  |  |
| Color of Core: - 1Core Cables= Black - 3Cores Cables= Red, Yellow, Blue |  |  |  |  |  |
| Item | Description | Type | Quantity (m) | Spare (m) | Total (m) |
|  | C/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC |  |  |  |  |
|  | 3C×95 mm2 | I | 310 | 30 | 340 |
|  | Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC |  |  |  |  |
|  | 1C×95 mm2 | H | 10 | - | 10 |
| Total Cable |  |  |  |  | 350 |

| LV POWER CABLE (3PAHSE SYSTEM) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| D02 Insulation Grade - Service Voltage: 600/1000 V |  |  |  |  |  |  |
| Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |  |
| Insulation: XLPE |  |  |  |  |  |  |
| Binder Tape: If Required |  |  |  |  |  |  |
| Fillers : PVC |  |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |  |
| Armor: Multi-Core Cables : Galvanized Steel Wire Armor (SWA) Single Core Cables : Aluminum Wire Armor (AWA) |  |  |  |  |  |  |
| Other Sheath: PVC |  |  |  |  |  |  |
| Color of Core: - 3Cores Cables = Red, Yellow, Blue (3 Phases) - 3Cores + Neutral = Red, Yellow, Blue, Black - 3Cores + Earth = Red, Yellow, Blue, G/Y - 3Cores + Neutral + Earth = Red, Yellow, Blue, Black & G/Y |  |  |  |  |  |  |
| Item | Description | Type | Color Code | Quantity (m) | Spare (m) | Total (m) |
|  | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV Multi-Core with Lead Sheath) |  |  |  |  |  |
|  | 3C×2.5 mm2 | A | (1) | 900 | 90 | 990 |
|  | 3C×4 mm2 | A | (1) | 840 | 85 | 945 |
|  | 3C×6 mm2 | A | (1) | 1500 | 150 | 1650 |
|  | 3C×10 mm2 | A | (1) | 8140 | 820 | 8960 |
|  | 3C×16 mm2 | A | (1) | 3680 | 370 | 4050 |
|  | 3C×25 mm2 | A | (1) | 410 | 40 | 450 |
|  | 4C×10 mm2 | A | (2) | 250 | 25 | 275 |
|  | 4C×25 mm2 | A | (2) | 580 | 60 | 640 |
|  | 4C×16 mm2 | A | (2) | 675 | 67 | 745 |
|  | 3C×25+16 mm2 | A | (2) | 260 | 40 | 300 |
|  | 3C×50+25 mm2 | A | (2) | 745 | 75 | 820 |
|  | 3C×70+35 mm2 | A | (2) | 1090 | 100 | 1190 |
|  | 3C×120+70 mm2 | A | (2) | 1640 | 164 | 1800 |
|  | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV Multi-Core) |  |  |  |  |  |
|  | 3C×4 mm2 | B | (1) | 305 | 30 | 335 |
|  | 3C×25 mm2 | B | (1) | 430 | 40 | 470 |
|  | 3C×95 mm2 | B | (1) | 55 | 10 | 65 |
|  | 3C×185 mm2 | B | (1) | HOLD | 15 | 135 |
|  | 3C×35+16 mm2 | B | (1) | 75 | 10 | 85 |
|  | 3C×50+25 mm2 | B | (1) | 500 | 50 | 550 |
|  | 3C×70+35 mm2 | B | (1) | 155 | 20 | 175 |
|  | 3C×95+50 mm2 | B | (1) | 200 | 20 | 220 |
|  | 3C×120+70 mm2 | B | (1) | 560 | 40 | 600 |
|  | 3C×240+120 mm2 | B | (1) | 150 | 20 | 170 |
|  | 4C×4 mm2 | B | (2) | 470 | 50 | 520 |
|  | 4C×10 mm2 | B | (2) | 200 | 20 | 220 |
|  | 4C×16 mm2 | B | (2) | 460 | 46 | 510 |
|  | 4C×25 mm2 | B | (2) | 260 | 30 | 290 |
|  | 4C×35 mm2 | B | (2) | 220 | 30 | 250 |
|  | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV Single-Core) |  |  |  |  |  |
|  | 1C×300 mm2 | C | Black | 770 | 80 | 850 |
|  | 1C×150mm2 | B | Black | 120 | 15 | 125 |
|  | Fire Resistant or MICC Lighting Cable |  |  |  |  |  |
|  | 3C×120+70 mm2 | Z | - | HOLD | 45 | 465 |
| Total Cable |  |  |  |  |  | 26990 |

| LV POWER CABLE (1PAHSE SYSTEM) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Insulation Grade - Service Voltage: 600/1000 V |  |  |  |  |  |  |
| Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |  |
| D02 Insulation: XLPE |  |  |  |  |  |  |
| Binder Tape: If Required |  |  |  |  |  |  |
| Fillers : PVC |  |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |  |
| Armor: Multi-Core Cables : Galvanized Steel Wire Armor (SWA) Single Core Cables : Aluminum Wire Armor (AWA) |  |  |  |  |  |  |
| Other Sheath: PVC |  |  |  |  |  |  |
| Color of Core: - 1Core Cables = Black - 1Core + Neutral = Blue & Black - 1Core + Neutral + Earth = Blue, Black & G/Y - 2Cores Cables (for DC Cable)= Red & Black - 1Cores Cables (for DC + Cable)= Red - 1Cores Cables (for DC - Cable)= BLACK |  |  |  |  |  |  |
| Item | Description | Type | Color Code | Quantity (m) | Spare (m) | Total (m) |
|  | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV Multi-Core with Lead Sheath) |  |  |  |  |  |
|  | 2C×4 mm2 | A | (2) | 4120 | 410 | 4530 |
|  | 2C×16 mm2 | A | (2) | 840 | 85 | 925 |
|  | 3C×4 mm2 | A | (2) | 10 | 5 | 15 |
|  | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV Multi-Core) |  |  |  |  |  |
|  | 3C×2.5 mm2 | B | (3) | 174 | 20 | 194 |
|  | 3C×4 mm2 | B | (3) | 1204 | 116 | 1320 |
|  | 3C×6 mm2 | B | (3) | 0 | 15 | 120 |
|  | 3C×10 mm2 | B | (3) | 210 | 30 | 240 |
|  | 3C×50+25+25 mm2 | B | (3) | 675 | 67 | 750 |
|  | 2C×4 mm2 | B | (3) | 215 | 25 | 240 |
|  | 2C×6 mm2 | B | (4) | 175 | 25 | 200 |
|  | 2C×50 mm2 | B | (4) | 120 | 15 | 135 |
|  | 2C×95 mm2 | B | (4) | 120 | 15 | 135 |
|  | 2C×120 mm2 | B | (4) | 160 | 15 | 175 |
|  | 1C×150 mm2 | B | (5) | 60 | 5 | 65 |
|  | 1C×150 mm2 | B | (6) | 60 | 5 | 65 |
|  | 1C×185 mm2 | B | (5) | 70 | 10 | 80 |
|  | 1C×185 mm2 | B | (6) | 70 | 10 | 80 |
|  | 5C×10 mm2 | B | (4) | 700 | 70 | 770 |
|  | 5C×25 mm2 | B | (4) | 900 | 100 | 1000 |
| Total Cable |  |  |  |  |  | 9149 |

Note: Only cables of items 2.7 to 2.14 of this table shall be class 5.

| LV CONTROL CABLE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulation Grade - Service Voltage: 600/1000 V |  |  |  |  |  |
| Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |
| Insulation: PVC |  |  |  |  |  |
| D02 Binder Tape: If Required |  |  |  |  |  |
| Fillers : PVC |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |
| Armor: Galvanized Steel Wire Armor (SWA) |  |  |  |  |  |
| Other Sheath: PVC |  |  |  |  |  |
| Color of Core: Black with White Identification Numbers |  |  |  |  |  |
| Item | Description | Type | Quantity (m) | Spare (m) | Total (m) |
|  | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (Control Multi-Core with Lead Sheath) |  |  |  |  |
|  | 2C×4 mm2 | D | 8290 | 810 | 9100 |
|  | 6C×6 mm2 | D | 900 | 100 | 1000 |
|  | 7C×2.5 mm2 | D | 8440 | 860 | 9300 |
|  | 10C×2.5 mm2 | D | 660 | 60 | 720 |
|  | Cu/PVC/Bd/SWA/PVC - NYRY (Control Multi-Core) |  |  |  |  |
|  | 3C×2.5 mm2 | E | 620 | 60 | 680 |
|  | 3C×4 mm2 | E | 120 | 20 | 140 |
|  | 3C×6 mm2 | E | 180 | 20 | 200 |
|  | 5C×2.5 mm2 | E | 50 | 10 | 60 |
|  | 7C×2.5 mm2 | E | 90 | 10 | 100 |
|  | 9C×2.5 mm2 | E | 90 | 10 | 100 |
|  | 12C×2.5 mm2 | E | 540 | 60 | 600 |
|  | 14C×2.5 mm2 | E | 275 | 25 | 300 |
|  | 16C×2.5 mm2 | E | 300 | 30 | 330 |
|  | Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE) |  |  |  |  |
| 3.1 | 36C×1.5(12×3×1.5) mm2 | R | 990 | 110 | 1100 |
| Total Cable |  |  |  |  | 23730 |

| LV LIGHTING SYSTEM |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Insulation Grade - Service Voltage: 600/1000 V |  |  |  |  |  |  |
| D02 Conductor: Plain Annealed Stranded Copper (Class 2) |  |  |  |  |  |  |
| Insulation: XLPE |  |  |  |  |  |  |
| Binder Tape: If Required |  |  |  |  |  |  |
| Fillers : PVC |  |  |  |  |  |  |
| Bedding: Extruded PVC |  |  |  |  |  |  |
| Armor: Multi-Core Cables : Galvanized Steel Wire Armor (SWA) Single Core Cables : Aluminum Wire Armor (AWA) |  |  |  |  |  |  |
| Other Sheath: PVC |  |  |  |  |  |  |
| Color of Core: - 1Core Cables = Black - 1Core + Neutral = Blue & Black - 1Core + Neutral + Earth = Blue, Black & G/Y - 3Cores Cables = Red, Yellow, Blue (3 Phases) - 3Cores + Neutral = Red, Yellow, Blue, Black - 3Cores + Earth = Red, Yellow, Blue, G/Y - 3Cores + Neutral + Earth = Red, Yellow, Blue, Black & G/Y |  |  |  |  |  |  |
| Item | Description | Type | Color Code | Quantity (m) | Spare (m) | Total (m) |
|  | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV Multi-Core with Lead Sheath) |  |  |  |  |  |
|  | 3C×6 mm2 | A | (3) | 2430 | 570 | 3000 |
|  | 5C×10 mm2 | A | (7) | 530 | 120 | 650 |
|  | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV Multi-Core) |  |  |  |  |  |
|  | 3C×6 mm2 | B | (3) | 505 | 95 | 600 |
|  | 5C×10 mm2 | B | (7) | 210 | 40 | 250 |
|  | Cu/PVC/PVC - NYY (LV MULTI-CORE FOR LIGHTING) |  |  |  |  |  |
| 3.1 | 3C×2.5 mm2 | L | (3) | 865 | 90 | 955 |
|  | Fire Resistant or MICC Lighting Cable |  |  |  |  |  |
| 4.1 | 3C×2.5 mm2 | Z | (3) | 250 | 30 | 280 |
| Total Cable |  |  |  |  |  | 5735 |

| Required Power Cable for GCS |  |  |
| --- | --- | --- |
| Item | Cable Type | Quantity (m) |
| 1 | 11 KV Power Cable | 1350 |
| 2 | 3.3 KV Power Cable | 350 |
| 3 | LV Power Cable (3pahse System) | 26990 |
| 4 | LV Power Cable (1pahse System) | 9149 |
| 5 | LV Control Cable | 23730 |
| 6 | LV Lighting System | 5735 |
| Total |  | 67304 |

Notes:

- This document shall be Based on below references:

Document Title: “Specification for Power & Control Cables”

Document No.: “BK-GNRAL-PEDCO-000-EL-SP-0014”

Document Title: “Data Sheets for Power & Control Cables”

Document No.: “BK-GCS-PEDCO-120-EL-DT-0010”

Document Title: “Electrical Power & Control Cable Schedule”

Document No.: “BK-GCS-PEDCO-120-EL-LI-0002”