## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-MT-0003_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-2524 |  |  | Transmital Date: 27-Dec-2023
Document Title: MTO For Power & Control Cables |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0210-EL-TR-2524 |  |  | Transmital Date: 27-Dec-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-MT-0003_D01 |  |  | CRS Status: | C2
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be issued after finalizing or minor comments on "Electrical Power & Control Cable Schedule" and "Area Electrical Cable Route & Section Layout". |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | در صورت هر گونه تغییر در مدارک پیش نیاز این مدرک به روز رسانی خواهد گردید.
2 | There is conflict between this document and "Electrical Power & Control Cable Schedule" from point of cable length, size and number of core view. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | لحاظ گردید.
3 | Considered spare part in tables of document for different size of cables shall be rechecked from contractual point of view base on scope of work & supply and spare part instruction and modified. (If required) |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | لحاظ گردید.
4 | It shall be clarify UV resistant for outer sheet has been mentioned base on which document. It seems it is not necessary for all cables base on electrical design criteria and specification. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | لحاظ گردید.
5 | Cable type of 1C×95 mm2 CU/XPLE/SWA/PVC shall be modified to CU/XPLE/AWA/PVC on page 4. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | لحاظ گردید.
6 | Cables type of section 5 on page 6 shall be modified to CU/XPLE/SWA/PVC instead of CU/XPLE/AWA/PVC. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | لحاظ گردید.
7 | Next revision of this document shall be submitted after finalizing or minor comments on prerequisite document as above mentioned comments. |  | BK-SUR-ENG-ELE-02-07794 | 2023-06-03 | در صورت هر گونه تغییر در مدارک پیش نیاز این مدرک به روز رسانی خواهد گردید.
8 | We have not received consultants response for above mentioned comments. So it shall be completed and suumitted by consultant in next revision. |  | BK-SUR-ENG-ELE-02-08935 | 2024-01-10 | در صورت هر گونه تغییر در مدارک پیش نیاز این مدرک به روز رسانی خواهد گردید.
9 | Red color for MV cable and black color for outer sheet shall be added same as previous version. It is necessary to add the color of outer sheet for MV and LV cables. |  | BK-SUR-ENG-ELE-02-08935 | 2024-01-10 | لحاظ گردید.
10 | There is conflict between this document and electrical cable schedule. It shall be rechecked and modified if required. For example cable 3x70+35 type B is not exist in cable list, control cable 7x2.5 type E cbale length shall be rechkced. More over 3x2.5 type E cable is not in this document. |  | BK-SUR-ENG-ELE-02-08935 | 2024-01-10 | لحاظ گردید.
11 | According to our telephone conversation 2 core cable for heater shall be rechecked and modified in this document and other related document such as electrical cable schedule. |  | BK-SUR-ENG-ELE-02-08935 | 2024-01-10 | لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-Jan-2024 |  |  |  |  | Date: