## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO For HVAC & Plumbing For Extension of Existing Elect. Building
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | HV | MT | 0002 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
MTO For HVAC & Plumbing For Extension of Existing Elect. Building نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | APR.2025 |  | IFI |  |  |  | K.Ahmadi |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  | FEB.2025 |  | IFI |  |  |  | K.Ahmadi |  |  | M.Fakharian |  | S.Faramarzpour
D01 |  | FEB.2025 |  | IFI |  |  |  | K.Ahmadi |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  | APR.2024 |  | IFI |  |  |  | K.Ahmadi |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: F8Z-708882
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO For HVAC & Plumbing For Extension of Existing Elect. Building
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از5
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | HV | MT | 0002 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 |  |  | X | [5 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## 1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO For HVAC & Plumbing For Extension of Existing Elect. Building
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه:3 از5
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | HV | MT | 0002 |  | D03
NON PAINTABLE GALVANIZED SHEET
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Noun paintable Galvanized sheet with 0.5 mm thickness. | [5 empty] | M2 |  | - |  | 15 | -
2 | Noun paintable Galvanized sheet with 0.6 mm thickness. | [5 empty] | M2 |  | - |  | 12 | -
SUPPLY AIR DIFFUSER
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Square four-way ceiling diffuser from extruded aluminum profile with 1.25mm thickness and anodized finish. | [5 empty] | Piece |  | 150*150 MM |  | 1 | -
2 | Square four-way ceiling diffuser from extruded aluminum profile with 1.25mm thickness and anodized finish. | [5 empty] | Piece |  | 300*300 MM |  | 1 | -
EXHAUST AIR GRILL
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Square egg crate grill from extruded aluminum profile with 1.25mm thickness and anodized finish. | [5 empty] | Piece |  | 150*150 MM |  | 1 | -
2 | Square egg crate grill from extruded aluminum profile with 1.25mm thickness and anodized finish. | [5 empty] | Piece |  | 400*400 MM |  | 1 | -
OPPOSED BLADE MANUAL VOLUME DAMPER
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Duct mounted opposed blade volume damper with 1.5mm thikness galvanized steel sheet for frames and blades. | [5 empty] | Piece |  | 150*100 MM |  | 1 | -
2 | Duct mounted opposed blade volume damper with 1.5mm thikness galvanized steel sheet for frames and blades. | [5 empty] | Piece |  | 150*150 MM |  | 1 | -
3 | Duct mounted opposed blade volume damper with 1.5mm thikness galvanized steel sheet for frames and blades. | [5 empty] | Piece |  | 300*200 MM |  | 1 | -
4 | Duct mounted opposed blade volume damper with 1.5mm thikness galvanized steel sheet for frames and blades. | [5 empty] | Piece |  | 400*150 MM |  | 1 | -
BLAST PROTECTION DAMPER
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Pre-Galvanized metal sheet according to BS EN 10346 blast protection damper with 3mm thickness fully welded casing, 2mm thickness blade, flange width and bolt hole drilling is according to ISO 15138 standard and 20mm diameter solid stainless steel 304 spindle. Maximum Pressure Drop = 105 Pa in 2.5 m/s air velocity. (Air Flow=181.3 L/S) | [5 empty] | Piece |  | 300*250 MM |  | 1 | -
2 | Pre-Galvanized metal sheet according to BS EN 10346 blast protection damper with 3mm thickness fully welded casing, 2mm thickness blade, flange width and bolt hole drilling is according to ISO 15138 standard and 20mm diameter solid stainless steel 304 spindle. Maximum Pressure Drop = 127 Pa in 3.3 m/s air velocity. (Air Flow=181.3 L/S) | [5 empty] | Piece |  | 400*150 MM |  | 1 | -

## 2
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO For HVAC & Plumbing For Extension of Existing Elect. Building
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه:4 از5
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | HV | MT | 0002 |  | D03
FIRE DAMPER
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Pre-Galvanized metal sheet according to BS EN 10346 fusible fire damper with 2mm thickness HAT channel frame, 2mm thickness 3V groove blade, 12.7mm diameter jackshaft, stainless steel jamb seals with UL stamped fusible link 74°C (165°F). Maximum Pressure Drop = 7.5 Pa. (Air Flow=181.3 L/S) | [5 empty] | Piece |  | 300*250 MM |  | 1 | -
2 | Pre-Galvanized metal sheet according to BS EN 10346 fusible fire damper with 2mm thickness HAT channel frame, 2mm thickness 3V groove blade, 12.7mm diameter jackshaft, stainless steel jamb seals with UL stamped fusible link 74°C (165°F). Maximum Pressure Drop = 8 Pa. (Air Flow=181.3 L/S) | [5 empty] | Piece |  | 400*150 MM |  | 2 | -
POLYPROPYLENE (PP) PIPE ACCORDING TO ASTM F2389 OR ISIRI 6314-1,2 AND FITTINGS FOR CONDENSATE PIPES
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Polypropylene (pp) pipe. | [5 empty] | M (length) |  | 25 MM |  | 56 | -
2 | Polypropylene (pp) pipe. | [5 empty] | M (length) |  | 32 MM |  | 24 | -
3 | Polypropylene (pp) elbow 90°. | [5 empty] | Piece |  | 25 MM |  | 7 | -
4 | Polypropylene (pp) elbow 90°. | [5 empty] | Piece |  | 32 MM |  | 4 | -
5 | Polypropylene (pp) equal Tee 90°. | [5 empty] | Piece |  | 25 MM |  | 4 | -
6 | Polypropylene (pp) equal Tee 90°. | [5 empty] | Piece |  | 32 MM |  | 1 | -
7 | Polypropylene (pp) unequal Tee 90°. | [5 empty] | Piece |  | 32*25*32 MM |  | 2 | -
8 | Polypropylene (pp) concentric reducer. | [5 empty] | Piece |  | 32*25 MM |  | 3 | -
9 | Polypropylene (pp) femail threaded coupler. | [5 empty] | Piece |  | 25 MM * 3/4" |  | 8 | -
10 | Polypropylene (pp) coupler. | [5 empty] | Piece |  | 25 MM |  | 4 | -
11 | Polypropylene (pp) coupler. | [5 empty] | Piece |  | 32 MM |  | 4 | -
12 | Flexible hose and other connectors for split unit condensate disposal system. | [5 empty] | Piece |  | 3/4" |  | 8 | -
T3 SPLIT DX COOLER ACCORDING TO THE PROJECT SPECIFICATIONS AND TECHNICAL DATA SHEET
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Procurement, transportation, installation and commissioning, indoor unit and outdoor unit wall mounted T3 split DX cooler with related wires, cables, refrigerant cooper tubes, supports and …, according to the project specifications and technical data sheet. | [5 empty] | Piece |  | 30000 BTU/HR |  | 2 | With thermostat and all standard accessory,cooling and heating (heat pump)
2 | Procurement, transportation, installation and commissioning, indoor unit and outdoor unit cassette T3 split DX cooler with related wires, cables, refrigerant cooper tubes, supports and …, according to the project specifications and technical data sheet. | [5 empty] | Piece |  | 36000 BTU/HR |  | 4 | With thermostat and all standard accessory,cooling and heating (heat pump)
3 | Procurement, transportation, installation and commissioning, indoor unit and outdoor unit cassette T3 split DX cooler with related wires, cables, refrigerant cooper tubes, supports and …, according to the project specifications and technical data sheet. | [5 empty] | Piece |  | 54000 BTU/HR |  | 4 | With thermostat and all standard accessory,cooling and heating (heat pump)
D03

## 3
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MTO For HVAC & Plumbing For Extension of Existing Elect. Building
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه:5 از5
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | HV | MT | 0002 |  | D03
FAN FILTER UNIT
Item | Description | [5 empty] | Unit |  | Size |  | Qty. | Remark
1 | Procurement, transportation, installation and commissioning, fan filter unit with related filters, dampers, DPT, sand trap louver, and …, according to the project specifications and technical data sheet. | [5 empty] | Piece |  | 181.3 L/S |  | 1 | -
UTILITY EXHAUST FAN
1 | Procurement, transportation, installation and commissioning, utility exhaust fan with related damper, and …, according to the project specifications and technical data sheet. | [5 empty] | Piece |  | 181.3 L/S |  | 1 | -