## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0002 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE SCHEDULE نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  |  | Apr.2025 |  | IFA |  |  |  | E.Zamani |  |  | M.Fakharian |  | S.Faramarzpour
D02 |  |  | Nov.2024 |  | IFA |  |  |  | M.Pourdasht |  |  | M.Fakharian |  | M.Sadeghian
D01 |  |  | Nov.2023 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | S.Faramarzpour
D00 |  |  | June.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F0Z-709067
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0002 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 51
2 | X | X | X |  | X |  |  |  | 52
3 | X | X | X |  | X |  |  |  | 53
4 | X | X | X |  | X |  |  |  | 54
5 | X | X | X |  | X |  |  |  | 55
6 | X | X | X |  | X |  |  |  | 56
7 | X | X | X |  | X |  |  |  | 57
8 | X | X | X |  | X |  |  |  | 58
9 | X | X | X |  | X |  |  |  | 59
10 |  | X | X |  | X |  |  |  | 60
11 |  | X | X |  | X |  |  |  | 61
12 |  | X | X |  | X |  |  |  | 62
13 |  | X | X |  | X |  |  |  | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX 1 2 3
(1) 1ST Group (Cable Type Commodity Code):
H: High Voltage Power Cable Uo/U (6/10 kV & 12/20 Kv & 18/30)
M: Medium Voltage Power Cable Uo/U ( 0.6/1 kV & up to 3.6/6 kV) |  |  |  | شماره صفحه: 1 از 13
L: Low Voltage Power Cable Uo/U (up to and including 0.6/1 kV)
C: Control Cables
I: Instrument Cable
(2) 2ND Group
From Equipment
(3) 3RD Group
Consumer Description: To Equipment Which will be fed.
2. CABLE TYPE
A: Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) |  | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH)
B: Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) |  | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE)
C: Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) |  | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE)
D: Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) |  | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH)
E: Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) |  | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE)
F: Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH) |  | F | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH)
F1: Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (HV MULTI-CORE WITH LEAD SHEATH) |  | F1 | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (HV MULTI-CORE WITH LEAD SHEATH)
G: Cu/SC/XLPE/SC/SCT/Lsh/Bd/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE WITH LEAD SHEATH) |  | G | Cu/SC/XLPE/SC/SCT/Lsh/Bd/AWA/PVC - N2XSYKYRY (MV SINGLE-CORE WITH LEAD SHEATH)
H: Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE) |  | H | Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE)
I: Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) |  | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE)
J: CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE) |  | J | CU/SM/XLPE/SM/SC/PVC/SWA/PVC - N2XSEYRY (HV MULTI-CORE)
K: CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE) |  | K | CU/SM/XLPE/SM/SC/PVC/AWA/PVC - N2XSYRY (HV SINGLE-CORE)
L: Cu/PVC/PVC - NYY (LV MULTI-CORE FOR LIGHTING) |  | L | Cu/PVC/PVC - NYY (LV MULTI-CORE FOR LIGHTING)
R: Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE) |  | R | Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE)
S: CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE OR EPR or H07 RN-F) |  | S | CU/XLPE/PVC - N2XY (LV SINGLE-CORE FLEXIBLE OR EPR or H07 RN-F)
Z: CU/MGT/XLPE/LSFOH/LSFOH (FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS … . ) |  | Z | CU/MGT/XLPE/LSFOH/LSFOH (FOR HAZARDOUS AREAS SUCH AS BATTERY ROOMS … . )
3. REFERANCE LIST
Area Electrical Cable Route & Section Layou | BK-GCS-PEDCO-120-EL-PY-0005
ELECTRICAL LOAD LIST | BK-GCS-PEDCO-120-EL-LI-0001
Existent MV Switchgear Expansion Single Line Diagram | BK-GCS-PEDCO-120-EL-SL-0003
LV Switchgear-MCC Single Line Diagram | BK-GCS-PEDCO-120-EL-SL-0002
Area Lighting & Small Power Layout | BK-GCS-PEDCO-120-EL-PY-0003
Electrical IO Signal List | BK-GCS-PEDCO-120-EL-LI-0005
Calculation Note for cable sizing | BK-GCS-PEDCO-120-EL-CN-0003
Electrical Typical Schematic Diagrams for LV Panel | BK-GCS-PEDCO-120-EL-DG-0002
Electrical Typical Schematic Diagrams for MV panel | BK-GCS-PEDCO-120-EL-DG-0001
Distribution & Lighting Panels Single Line Diagram | BK-GCS-PEDCO-120-EL-SL-0004
Notes:
1- The control cable of IRP Pump will be supplied by vendor
Reference documents are as below:
The reference documents For Cable OD is abhar and gland size is S.E.M.C manufacture
تسهیلات
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره صفحه: 3 از 12
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0002
D03
بسته کاری
GCS
پروژه
BK

## GCS
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (mm) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type |  | Description | Rout
|  |  |  | FROM | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D03 | H-11SWGA-TR001 | 11 | GCS-11-SWG-001A | GCS-TR-001 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Transformer-001 11/.42 KV
2 | D03 | C-11SWGA-RCP-01 | 0.11DC | GCS-11-SWG-001A | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | From 11KV Switchgear A to RCP
3 | D02 | L-NSWGA-TR001-A1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
4 | D02 | L-NSWGA-TR001-A2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
5 | D02 | L-NSWGA-TR001-A3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear |  | شماره صفحه: 1 از 12
6 | D02 | L-NSWGA-TR001-A4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
7 | D02 | L-NSWGA-TR001-B1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
8 | D02 | L-NSWGA-TR001-B2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
9 | D02 | L-NSWGA-TR001-B3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
10 | D02 | L-NSWGA-TR001-B4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
11 | D02 | L-NSWGA-TR001-C1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
12 | D02 | L-NSWGA-TR001-C2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
13 | D02 | L-NSWGA-TR001-C3 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
14 | D02 | L-NSWGA-TR001-C4 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
15 | D02 | L-NSWGA-TR001-N1 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
16 | D02 | L-NSWGA-TR001-N2 | 0.4 | GCS-400-NSWG-001A | GCS-TR-001 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 001 to LV Switchgear
17 | D01 | C-NSWGA-TR001-1 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Transformer 001 Mechanical Protection
18 | D02 | C-NSWGA-TR001-2 | - | GCS-400-NSWG-001A | GCS-TR-001 | - | 3×6 | 3C | 6 | - | - | 20 | M20 A | M20 A | 16.8 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Neutral CT of Transformer 001
19 | D01 | C-NSWGA-TR001-3 | 0.11DC | GCS-400-NSWG-001A | GCS-TR-001 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Interlock/Intertrip to Upstrem
20 | D03 | H-11SWGB-TR002 | 11 | GCS-11-SWG-001B | GCS-TR-002 | 1250KVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Transformer-002 11/.42 KV
21 | D03 | C-11SWGB-RCP-02 | 0.11DC | GCS-11-SWG-001B | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | From 11KV Switchgear B to RCP
22 | D02 | L-NSWGB-TR002-A1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
23 | D02 | L-NSWGB-TR002-A2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
24 | D02 | L-NSWGB-TR002-A3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
25 | D02 | L-NSWGB-TR002-A4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
26 | D02 | L-NSWGB-TR002-B1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
27 | D02 | L-NSWGB-TR002-B2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
28 | D02 | L-NSWGB-TR002-B3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
29 | D02 | L-NSWGB-TR002-B4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
30 | D02 | L-NSWGB-TR002-C1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
31 | D02 | L-NSWGB-TR002-C2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
32 | D02 | L-NSWGB-TR002-C3 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
33 | D02 | L-NSWGB-TR002-C4 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | 300 | - | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
34 | D02 | L-NSWGB-TR002-N1 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
35 | D02 | L-NSWGB-TR002-N2 | 0.4 | GCS-400-NSWG-001B | GCS-TR-002 | 1250KVA | 1×300 | 1C | - | 300 | - | 20 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | from Secondary Side of Transformer 002 to LV Switchgear
36 | D01 | C-NSWGA-TR002-1 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 20 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Transformer 002 Mechanical Protection
37 | D02 | C-NSWGA-TR002-2 | - | GCS-400-NSWG-001B | GCS-TR-002 | - | 3×6 | 3C | 6 | - | - | 20 | M20 A | M20 A | 16.8 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Neutral CT of Transformer 002
38 | D01 | C-NSWGA-TR002-3 | 0.11DC | GCS-400-NSWG-001B | GCS-TR-002 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Interlock/Intertrip to Upstrem
39 | D03 | H-11SWGB-TR003 | 11 | GCS-11-SWG-001B | GCS-TR-03 | 800 kVA | 3×95 | 3C | 95 | - | - | 70 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | from Switchgear 11SWGB to Fire Water Transformer 003
40 | D03 | C-11SWGB-RCP-03 | 0.11DC | GCS-11-SWG-001B | RCP | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | From 11SWGB Switchgear to RCP for Fire Water
41 | D01 | M-TR003-NGR | 3.3 | GCS-TR-003 | GCS-3.3-NGR-01 | - | 1×95 | 1C | 95 | - | - | 10 | M40 | M40 | 35.7 | H | Cu/SC/XLPE /SC/SCT/CWS/Bd/AWA/PVC - N2XSYRY (MV SINGLE-CORE) | NGR
42 | D01 | C-3.3SWG-TR003-1 | 0.11DC | GCS-3.3-SWG-001 | GCS-TR-03 | - | 12×2.5 | 12C | 2.5 | - | - | 70 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Transformer 003 Mechanical Protection
43 | D02 | C-3.3SWG-TR003-2 | - | GCS-3.3-SWG-001 | GCS-TR-03 |  | 3×6 | 3C | 6 | - | - | 70 | M20 A | M20 A | 16.8 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Neutral CT of Transformer 003 for 51G
44 | D02 | C-3.3SWG-TR003-3 | - | GCS-3.3-SWG-001 | GCS-TR-03 |  | 3×6 | 3C | 6 | - | - | 70 | M20 A | M20 A | 16.8 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Neutral CT of Transformer 003 for 64REF
45 | D03 | M-3.3SWG-TR003 | 3.3 | GCS-TR-03 | GCS-3.3-SWG-001 | - | 3×120 | 3C | 95 | - | - | 60 | M75 | M75 | 68.8 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | from 3.3 Switchgear to Transformer 003
46 | D01 | M-3.3SWG-P2301A | 3.3 | GCS-3.3-SWG-001 | P-2301A | 300 | 3×95 | 3C | 95 | - | - | 250 | M75 | M75 | 68.8 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Fire Water Electric Pump
47 | D03 | C-3.3SWG-LCS | 0.11DC | GCS-3.3-SWG-001 | P-2301A | - | 16×2.5 | 16C | 2.5 | - | - | 250 | M32 | M32 | 33 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | LCS for P-2301A
48 | D02 | C-3.3SWG-IRP-01 | 0.23 | GCS-3.3-SWG-001 | IRP-DCS | - | 5×2.5 | 5C | 2.5 | 2.5 | 2.5 | 25 | M25 | M25 | 21.6 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for P-2301A
49 | D02 | C-3.3SWG-IRP-02 | 0.23 | GCS-3.3-SWG-001 | IRP-F&G | - | 5×2.5 | 5C | 2.5 | 2.5 | 2.5 | 25 | M25 | M25 | 21.6 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-F&G for P-2301A
50 | D03 | H-11SWGA-C2101-A | 11 | GCS-11-SWG-001A | C-2101A | 1070 | 3×95 | 3C | 95 | - | - | 270 | M90 | M90 EX | 87.7 | F | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH) | First & Second Stage Gas Compressor C-2101A
51 | D03 | L-11SWGA-SPH-A | 0.23 | GCS-11-SWG-001A | Space Heater | 0.3 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 270 | M20 | M20 EX | 15.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Space Heater for Gas Compressor C-2101A
52 | D03 | C-11SWGA-IRP-A | 0.11DC | GCS-11-SWG-001A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Gas Compressor C-2101A
53 | D02 | C-11SWGA-IRP-A (ESD) | 0.11DC | GCS-11-SWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 40 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (ESD) for Gas Compressor C-2101A
54 | D03 | C-11SWGA-IRP-A (DCS) | 0.11DC | GCS-11-SWG-001A | IRP-DCS | - | 3×4 | 3C | 4 | - | - | 40 | M20 | M20 | 16.6 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (DCS) for Gas Compressor C-2101A
55 | D02 | C-11SWGA-C2101-A | - | GCS-11-SWG-001A | C-2101A | - | 5×4 | 5C | 4 | 4 | 4 | 270 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS (Ammeter+stop cammand) for Gas Compressor C-2101A
56 | D02 | C-11SWGA-RTD2101-A1 | - | UCP-A | C-2101A | - | 12×(3×1.5) | 3C | 1.5 | - | - | 300 | M50 | M50 EX | 41 | R | Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE) | RTD for Gas Compressor C-2101A (From Control Room for Stator)
57 | D02 | C-11SWGA-RTD2101-A2 | - | UCP-A | C-2101A | - | 3×3×1.5 | 9C | 1.5 | - | - | 0 | M32 | M32EX |  |  |  | RTD for Gas Compressor C-2101A (From Control Room for beraing)
58 | D02 | C-11SWGA-DF2101-A | - | GCS-11-SWG-001A | C-2101A | - | 6×6 | 6C | 6 | - | - | 270 | M32 | M32 EX | - | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Differential Protection of C-2101A
59 | D03 | H-11SWGA-CAP-A | 11 | GCS-11-SWG-001A | Cap Bank A | 530 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Capacitor Bank for Gas Compressor C-2101A
60 | D02 | C-11SWGA-CAP-A | 0.11DC | GCS-11-SWG-001A | Cap Bank A | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Control for Capacitor Bank of C-2101A
61 | D03 | L-NSWGA-MCC2101A | 0.4 | GCS-400-NSWG-001A | MCC-2101A | 43.9 | 3×35+16+16 | 5C | 35 | 16 | 16 | 25 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Normal Panel for Gas Compressor C-2101A (Auxiliary)
62 | D02 | L-MCC2101A-OH | 0.23 | MCC-2101A | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 250 | M25 | M32 EX | 21.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Heater for Gas Compressor C-2101A
63 | D03 | C-MCC2101A-OH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Oil Heater C-2101A
64 | D02 | L-MCC2101A-BR | 0.4 | MCC-2101A | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 250 | M25 | M25 EX | 23.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Barring Device Motor for Gas Compressor C-2101A
65 | D03 | C-MCC2101A-BR01 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Barring Device Motor C-2101A
66 | D02 | C-MCC2101A-BR02 | - | MCC-2101A | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Barring Device Motor C-2101A
67 | D02 | L-MCC2101A-AP | 0.4 | MCC-2101A | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Pump for Gas Compressor C-2101A (P-2101-AP A)
68 | D03 | C-MCC2101A-AP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Oil Pump C-2101A
69 | D02 | C-MCC2101A-AP2 | - | MCC-2101A | Oil Pump | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Oil Pump C-2101A
70 | D02 | L-MCC2101A-OC | 0.4 | MCC-2101A | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Lube Oil Cooler for Gas Compressor C-2101A (AE-2101-OC A)
71 | D03 | C-MCC2101A-OC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Lube Oil Cooler C-2101A
72 | D02 | C-MCC2101A-OC2 | - | MCC-2101A | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Lube Oil Cooler Motor C-2101A
73 | D02 | L-MCC2101A-LP | 0.4 | MCC-2101A | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 250 | M20 A | M20 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Pump for Gas Compressor C-2101A (M-2101-LP A)
74 | D03 | C-MCC2101A-LP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Cylinder Lubricator Pump C-2101A
75 | D02 | C-MCC2101A-LP2 | - | MCC-2101A | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Cylinder Lubricator Pump C-2101A
76 | D02 | L-MCC2101A-LH | 0.23 | MCC-2101A | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 250 | M20 A | M20 EX | 21 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Oil Heater for Gas Compressor C-2101A
77 | D03 | C-MCC2101A-LH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Cylinder Lubricator Oil Heater C-2101A
78 | D02 | L-MCC2101A-AX | 0.4 | MCC-2101A | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Aux Pump Motor for Gas Compressor C-2101A (P-2101-AX A)
79 | D03 | C-MCC2101A-AX1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Aux Pump Motor C-2101A
80 | D02 | C-MCC2101A-AX2 | - | MCC-2101A | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Aux Pump Motor C-2101A
81 | D02 | L-MCC2101A-WP | 0.4 | MCC-2101A | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 250 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Main Pump Motor for Gas Compressor C-2101A (P-2101-WP A)
82 | D03 | C-MCC2101A-WP1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Main Pump Motor C-2101A
83 | D02 | C-MCC2101A-WP2 | - | MCC-2101A | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Main Pump Motor C-2101A
84 | D02 | L-MCC2101A-WH | 0.4 | MCC-2101A | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 250 | M50 | M50 EX | 47.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Electric Heater for Gas Compressor C-2101A (P-2101-WH A)
85 | D03 | C-MCC2101A-WH | 0.23 | MCC-2101A | IRP (UCP-A) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Electric Heater C-2101A
86 | D02 | L-MCC2101A-WC | 0.4 | MCC-2101A | Water Console | 4 | 3×10 | 3C | 10 | - | - | 250 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Water Console Cooler Motor for Gas Compressor C-2101A (AE-2101-WC A)
87 | D03 | C-MCC2101A-WC1 | 0.23 | MCC-2101A | IRP (UCP-A) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-A) for Water Console Cooler Motor C-2101A
88 | D02 | C-MCC2101A-WC2 | - | MCC-2101A | Water Console | - | 2×4 | 2C | 4 | - | - | 250 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101A
89 | D03 | C-MCC2101A-EHT | 0.4 | MCC-2101A | Heat Trace A | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Electrcial Heat Trace for Compressor A | HOLD
90 | D03 | H-11SWGB-C2101-B | 11 | GCS-11-SWG-001B | C-2101B | 1070 | 3×95 | 3C | 95 | - | - | 300 | M90 | M90 EX | 87.7 | F | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH) | First & Second Stage Gas Compressor C-2101B
91 | D03 | L-11SWGB-SPH-B | 0.23 | GCS-11-SWG-001B | Space Heater | 0.3 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 300 | M20 | M20 EX | 15.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Space Heater for Gas Compressor C-2101B
92 | D03 | C-11SWGB-IRP-B | 0.11DC | GCS-11-SWG-001B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Gas Compressor C-2101B
93 | D02 | C-11SWGB-IRP-B (ESD) | 0.11DC | GCS-11-SWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (ESD) for Gas Compressor C-2101B
94 | D03 | C-11SWGA-IRP-B (DCS) | 0.11DC | GCS-11-SWG-001B | IRP-DCS | - | 3×4 | 3C | 4 | - | - | 40 | M20 | M20 | 16.6 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (DCS) for Gas Compressor C-2101B
95 | D02 | C-11SWGB-C2101-B | - | GCS-11-SWG-001B | C-2101B | - | 5×4 | 5C | 4 | 4 | 4 | 300 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS (Ammeter+stop cammand) for Gas Compressor C-2101B
96 | D02 | C-11SWGB-RTD2101-B1 | - | UCP-B | C-2101B | - | 12×(3×1.5) | 3C | 1.5 | - | - | 330 | M50 | M50 EX | 41 | R | Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE) | RTD for Gas Compressor C-2101B (From Control Room for Stator)
97 | D02 | C-11SWGB-RTD2101-B2 | - | UCP-B | C-2101B | - | 3×3×1.5 | 9C | 1.5 | - | - | 0 | M32 | M32EX |  |  |  | RTD for Gas Compressor C-2101B (From Control Room for beraing)
98 | D02 | C-11SWGB-DF2101-B | - | GCS-11-SWG-001B | C-2101B | - | 6×6 | 6C | 6 | - | - | 300 | M25 | M25 EX | - | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Differential Protection of C-2101B
99 | D03 | H-11SWGB-CAP-B | 11 | GCS-11-SWG-001B | Cap Bank B | 530 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Capacitor Bank for Gas Compressor C-2101B
100 | D02 | C-11SWGB-CAP-B | 0.11DC | GCS-11-SWG-001B | Cap Bank B | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Control for Capacitor Bank of C-2101B
101 | D03 | L-NSWGB-MCC2101B | 0.4 | GCS-400-NSWG-001B | MCC-2101B | 43.9 | 3×35+16+16 | 5C | 35 | 16 | 16 | 25 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Normal Panel for Gas Compressor C-2101B (Auxiliary)
102 | D02 | L-MCC2101B-OH | 0.23 | MCC-2101B | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 280 | M25 | M32 EX | 21.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Heater for Gas Compressor C-2101B
103 | D03 | C-MCC2101B-OH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Oil Heater C-2101B
104 | D02 | L-MCC2101B-BR | 0.4 | MCC-2101B | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 280 | M25 | M25 EX | 23.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Barring Device Motor for Gas Compressor C-2101B
105 | D03 | C-MCC2101B-BR1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Barring Device Motor C-2101B
106 | D02 | C-MCC2101B-BR2 | - | MCC-2101B | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Barring Device Motor for Gas Compressor C-2101B
107 | D02 | L-MCC2101B-AP | 0.4 | MCC-2101B | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Pump for Gas Compressor C-2101B (P-2101-AP B)
108 | D03 | C-MCC2101B-AP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Oil Pump C-2101B
109 | D02 | C-MCC2101B-AP2 | - | MCC-2101B | Oil Pump | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Oil Pump for Gas Compressor C-2101B
110 | D02 | L-MCC2101B-OC | 0.4 | MCC-2101B | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Lube Oil Cooler for Gas Compressor C-2101B (AE-2101-OC B)
111 | D03 | C-MCC2101B-OC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Lube Oil Cooler C-2101B
112 | D02 | C-MCC2101B-OC2 | - | MCC-2101B | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Lube Oil Cooler for Gas Compressor C-2101B
113 | D02 | L-MCC2101B-LP | 0.4 | MCC-2101B | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Pump for Gas Compressor C-2101B (M-2101-LP B)
114 | D03 | C-MCC2101B-LP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Cylinder Lubricator Pump C-2101B
115 | D02 | C-MCC2101B-LP2 | - | MCC-2101B | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Cylinder Lubricator Pump for Gas Compressor C-2101B
116 | D02 | L-MCC2101B-LH | 0.23 | MCC-2101B | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 280 | M25 | M25 EX | 21 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Oil Heater for Gas Compressor C-2101B
117 | D03 | C-MCC2101B-LH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Cylinder Lubricator Oil Heater C-2101B
118 | D02 | L-MCC2101B-AX | 0.4 | MCC-2101B | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Aux Pump for Gas Compressor C-2101B (P-2101-AX B)
119 | D03 | C-MCC2101B-AX1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Aux Pump Motor C-2101B
120 | D02 | C-MCC2101B-AX2 | - | MCC-2101B | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Aux Pump for Gas Compressor C-2101B
121 | D02 | L-MCC2101B-WP | 0.4 | MCC-2101B | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 280 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Main Pump for Gas Compressor C-2101B (P-2101-WP B)
122 | D03 | C-MCC2101B-WP1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Main Pump Motor C-2101B
123 | D02 | C-MCC2101B-WP2 | - | MCC-2101B | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Main Pump for Gas Compressor C-2101B
124 | D02 | L-MCC2101B-WH | 0.4 | MCC-2101B | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 280 | M50 | M50 EX | 47.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Electric Heater for Gas Compressor C-2101B (P-2101-WH B)
125 | D03 | C-MCC2101B-WH | 0.23 | MCC-2101B | IRP (UCP-B) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) for Electric Heater C-2101B
126 | D02 | L-MCC2101B-WC | 0.4 | MCC-2101B | Water Console | 4 | 3×10 | 3C | 10 | - | - | 280 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Water Console Cooler Motor for Gas Compressor C-2101B (AE-2101-WC B)
127 | D03 | C-MCC2101B-WC1 | 0.23 | MCC-2101B | IRP (UCP-B) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-B) forWater Console Cooler Motor C-2101B
128 | D02 | C-MCC2101B-WC2 | - | MCC-2101B | Water Console | - | 2×4 | 2C | 4 | - | - | 280 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101B
129 | D03 | C-MCC2101B-EHT | 0.4 | MCC-2101B | Heat Trace B | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | D | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Electrcial Heat Trace for Compressor B | HOLD
130 | D03 | H-11SWGA-C2101-C | 11 | GCS-11-SWG-001A | C-2101C | 1070 | 3×95 | 3C | 95 | - | - | 330 | M90 | M90 EX | 87.7 | F | Cu/SC/XLPE/SC/SCT/Lsh/Bd/SWA/PVC - N2XSEYKYRY (MV MULTI-CORE WITH LEAD SHEATH) | First & Second Stage Gas Compressor C-2101C
131 | D03 | L-11SWGC-SPH-C | 0.23 | GCS-11-SWG-001C | Space Heater | 0.3 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 330 | M20 | M20 EX | 15.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Space Heater for Gas Compressor C-2101C
132 | D03 | C-11SWGC-IRP-C | 0.11DC | GCS-11-SWG-001C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 40 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Gas Compressor C-2101C
133 | D02 | C-11SWGC-IRP-C (ESD) | 0.11DC | GCS-11-SWG-001C | IRP-ESD | - | 3×2.5 | 3C | 2.5 | - | - | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (ESD) for Gas Compressor C-2101C
134 | D03 | C-11SWGA-IRP-C (DCS) | 0.11DC | GCS-11-SWG-001C | IRP-DCS | - | 3×4 | 3C | 4 | - | - | 40 | M20 | M20 | 16.6 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (DCS) for Gas Compressor C-2101C
135 | D02 | C-11SWGC-C2101-C | - | GCS-11-SWG-001C | C-2101C | - | 5×4 | 5C | 4 | 4 | 4 | 330 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS (Ammeter+stop cammand) for Gas Compressor C-2101C
136 | D02 | C-11SWGC-RTD2101-C1 | - | UCP-C | C-2101C | - | 12×(3×1.5) | 3C | 1.5 | - | - | 360 | M50 | M50 EX | 41 | R | Cu/PVC/OSCR/Bd/LSH/Bd/SWA/PVC (RTD CABLE) | RTD for Gas Compressor C-2101C (From Control Room for Stator)
137 | D02 | C-11SWGC-RTD2101-C2 |  | UCP-C | C-2101C |  | 3×3×1.5 | 9C | 1.5 |  |  | 0 | M32 | M32 EX |  |  |  | RTD for Gas Compressor C-2101C (From Control Room for Bearing)
138 | D02 | C-11SWGC-2101-C | - | GCS-11-SWG-001C | C-2101C | - | 6×6 | 6C | 6 | - | - | 330 | M25 | M25 EX | - | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Differential Protection of C-2101C
139 | D03 | H-11SWGA-CAP-C | 11 | GCS-11-SWG-001A | Cap Bank C | 530 kvar | 3×95 | 3C | 95 | - | - | 30 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | Capacitor Bank for Gas Compressor C-2101C
140 | D02 | C-11SWGC-CAP-C | 0.11DC | GCS-11-SWG-001C | Cap Bank C | - | 7×2.5 | 7C | 2.5 | - | - | 30 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Control for Capacitor Bank of C-2101C
141 | D03 | L-NSWGC-MCC2101B | 0.4 | GCS-400-NSWG-001B | MCC-2101C | 43.9 | 3×35+16+16 | 5C | 35 | 16 | 16 | 25 | M32 | M32 | 32.1 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Normal Panel for Gas Compressor C-2101C (Auxiliary)
142 | D02 | L-MCC2101C-OH | 0.23 | MCC-2101C | Oil Heater | 1.5 | 2×16 | 2C | 16 | 16 | - | 310 | M25 | M32 EX | 21.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Heater for Gas Compressor C-2101C
143 | D03 | C-MCC2101C-OH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Oil Heater C-2101C
144 | D02 | L-MCC2101C-BR | 0.4 | MCC-2101C | Barring Device Motor | 2.2 | 3×6 | 3C | 6 | - | - | 310 | M25 | M25 EX | 23.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Barring Device Motor for Gas Compressor C-2101C
145 | D03 | C-MCC2101C-BR1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Barring Device Motor C-2101C
146 | D02 | C-MCC2101C-BR2 | - | MCC-2101C | Barring Device Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Barring Device Motor for Gas Compressor C-2101C
147 | D02 | L-MCC2101C-AP | 0.4 | MCC-2101C | Oil Pump | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Oil Pump for Gas Compressor C-2101C (P-2101-AP C)
148 | D03 | C-MCC2101C-AP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Oil Pump C-2101C
149 | D02 | C-MCC2101C-AP2 | - | MCC-2101C | Oil Pump | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Oil Pump for Gas Compressor C-2101C
150 | D02 | L-MCC2101C-OC | 0.4 | MCC-2101C | Oil Cooler | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Lube Oil Cooler for Gas Compressor C-2101C (AE-2101-OC C)
151 | D03 | C-MCC2101C-OC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Lube Oil Cooler C-2101C
152 | D02 | C-MCC2101C-OC2 | - | MCC-2101C | Oil Cooler | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Lube Oil Cooler for Gas Compressor C-2101C
153 | D02 | L-MCC2101C-LP | 0.4 | MCC-2101C | Lubricator Pump | 0.55 | 3×4 | 3C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Pump for Gas Compressor C-2101C (M-2101-LP C)
154 | D03 | C-MCC2101C-LP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Cylinder Lubricator Pump C-2101C
155 | D02 | C-MCC2101C-LP2 | - | MCC-2101C | Lubricator Pump | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Cylinder Lubricator for Gas Compressor C-2101C
156 | D02 | L-MCC2101C-LH | 0.23 | MCC-2101C | Lubricator Heater | 0.4 | 2×4 | 2C | 4 | 4 | - | 310 | M25 | M25 EX | 21 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cylinder Lubricator Oil Heater for Gas Compressor C-2101C
157 | D03 | C-MCC2101C-LH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Cylinder Lubricator Oil Heater C-2101C
158 | D02 | L-MCC2101C-AX | 0.4 | MCC-2101C | Aux Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Aux Pump Motor for Gas Compressor C-2101B (P-2101-AX C)
159 | D03 | C-MCC2101C-AX1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Aux Pump Motor C-2101C
160 | D02 | C-MCC2101C-AX2 | - | MCC-2101C | Aux Pump Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Aux Pump Motor for Gas Compressor C-2101C
161 | D02 | L-MCC2101C-WP | 0.4 | MCC-2101C | Main Pump Motor | 7.5 | 3×16 | 3C | 16 | - | - | 310 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Main Pump Motor for Gas Compressor C-2101C (P-2101-WP C)
162 | D03 | C-MCC2101C-WP1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Main Pump Motor C-2101C
163 | D02 | C-MCC2101C-WP2 | - | MCC-2101C | Main Pump Motor | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Main Pump Motor for Gas Compressor C-2101C
164 | D02 | L-MCC2101C-WH | 0.4 | MCC-2101C | Electric Heater | 12 | 3×70+35 | 4C | 70 | 35 | - | 310 | M50 | M50 EX | 47.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Electric Heater for Gas Compressor C-2101B (P-2101-WH C)
165 | D03 | C-MCC2101C-WH | 0.23 | MCC-2101C | IRP (UCP-C) | - | 9×2.5 | 9C | 2.5 | - | - | 10 | M32 | M32 | 29 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Electric Heater C-2101C
166 | D02 | L-MCC2101C-WC | 0.4 | MCC-2101C | Water Console | 4 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Water Console Cooler Motor for Gas Compressor C-2101C (AE-2101-WC C)
167 | D03 | C-MCC2101C-WC1 | 0.23 | MCC-2101C | IRP (UCP-C) | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP (UCP-C) for Water Console Cooler Motor C-2101C
168 | D02 | C-MCC2101C-WC2 | - | MCC-2101C | Water Console | - | 2×4 | 2C | 4 | - | - | 310 | M25 | M25 EX | 22.6 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for Water Console Cooler Motor for Gas Compressor C-2101C
169 | D03 | C-MCC2101C-EHT | 0.4 | MCC-2101B | Heat Trace C | - | 5x25 | 5C | 25 | 25 | 25 | 300 | M32 | M32 | 32.1 | D | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Electrcial Heat Trace for Compressor C | HOLD
170 | D02 | L-NSWGA-AC2121A-1 | 0.4 | GCS-400-NSWG-001A | AC-2121A | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121A
171 | D03 | C-NSWGA-AC2121A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2121A
172 | D02 | C-NSWGA-AC2121A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2121A
173 | D03 | C-NSWGA-AC2121A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 310 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2121A
174 | D03 | C-NSWGA-AC2121A-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2121A
175 | D03 | L-NSWGA-AC2121A-2 | 0.4 | GCS-400-NSWG-001A | AC-2121A | 5.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121A
176 | D03 | C-NSWGA-AC2122A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2122A
177 | D02 | C-NSWGA-AC2122A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2122A
178 | D03 | C-NSWGA-AC2122A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 310 | M32 | M32 EX | 29 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2122A
179 | D03 | C-NSWGA-AC2122A-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2122A
180 | D02 | L-NSWGB-AC2121B-1 | 0.4 | GCS-400-NSWG-001B | AC-2121B | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121B
181 | D03 | C-NSWGB-AC2121B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2121B
182 | D02 | C-NSWGB-AC2121B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2121B
183 | D03 | C-NSWGB-AC2121B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 340 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2121B
184 | D03 | C-NSWGA-AC2121B-04 | - | GCS-400-NSWG-001B | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2121B
185 | D03 | L-NSWGB-AC2121B-2 | 0.4 | GCS-400-NSWG-001B | AC-2121B | 5.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121B
186 | D03 | C-NSWGB-AC2122B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2122B
187 | D02 | C-NSWGB-AC2122B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2122B
188 | D03 | C-NSWGB-AC2122B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 340 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2122B
189 | D03 | C-NSWGA-AC2122B-04 | - | GCS-400-NSWG-001B | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2122B
190 | D02 | L-NSWGA-AC2121C-1 | 0.4 | GCS-400-NSWG-001A | AC-2121C | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121C
191 | D03 | C-NSWGA-AC2121C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2121C
192 | D02 | C-NSWGA-AC2121C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2121C
193 | D03 | C-NSWGA-AC2121C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2121C
194 | D03 | C-NSWGA-AC2121C-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2121C
195 | D03 | L-NSWGA-AC2121C-2 | 0.4 | GCS-400-NSWG-001A | AC-2121C | 5.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Stage Air Cooler 2121C
196 | D03 | C-NSWGA-AC2122C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2122C
197 | D02 | C-NSWGA-AC2122C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2122C
198 | D03 | C-NSWGA-AC2122C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2122C
199 | D03 | C-NSWGA-AC2122C-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2122C
200 | D02 | L-NSWGA-AC2131A-1 | 0.4 | GCS-400-NSWG-001A | AC-2131A | 7.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2131A
201 | D03 | C-NSWGA-AC2131A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2131A
202 | D02 | C-NSWGA-AC2131A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2131A
203 | D03 | C-NSWGA-AC2131A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 310 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2131A
204 | D03 | C-NSWGA-AC2131A-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2131A
205 | D03 | L-NSWGA-AC2131A-2 | 0.4 | GCS-400-NSWG-001A | AC-2131A | 7.5 | 3×10 | 3C | 10 | - | - | 310 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2131A
206 | D03 | C-NSWGA-AC2132A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2132A
207 | D02 | C-NSWGA-AC2132A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2132A
208 | D03 | C-NSWGA-AC2132A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 310 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2132A
209 | D03 | C-NSWGA-AC2132A-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2132A
210 | D02 | L-NSWGB-AC2131B-1 | 0.4 | GCS-400-NSWG-001B | AC-2131B | 7.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2132A
211 | D03 | C-NSWGB-AC2131B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2132A
212 | D02 | C-NSWGB-AC2131B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2132A
213 | D03 | C-NSWGB-AC2131B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 340 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2132A
214 | D03 | C-NSWGA-AC2131B-04 | - | GCS-400-NSWG-001B | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2131B
215 | D02 | L-NSWGB-AC2131B-2 | 0.4 | GCS-400-NSWG-001B | AC-2131B | 7.5 | 3×10 | 3C | 10 | - | - | 340 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2131B
216 | D03 | C-NSWGB-AC2132B-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2132A
217 | D02 | C-NSWGB-AC2132B-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2132A
218 | D03 | C-NSWGB-AC2132B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 340 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2132A
219 | D03 | C-NSWGA-AC2132B-04 | 0.23 | GCS-400-NSWG-001B | - | - | 2×4 | 2C | 2.5 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2132B
220 | D02 | L-NSWGA-AC2131C-1 | 0.4 | GCS-400-NSWG-001A | AC-2131C | 7.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2131C
221 | D03 | C-NSWGA-AC2131C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2131C
222 | D02 | C-NSWGA-AC2131C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2131C
223 | D03 | C-NSWGA-AC2131C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2131C
224 | D03 | C-NSWGA-AC2131C-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2131C
225 | D03 | L-NSWGA-AC2131C-2 | 0.4 | GCS-400-NSWG-001A | AC-2131C | 7.5 | 3×10 | 3C | 10 | - | - | 370 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Second Stage Air Cooler 2131C
226 | D03 | C-NSWGA-AC2132C-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Air Cooler 2132C
227 | D02 | C-NSWGA-AC2132C-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Air Cooler 2132C
228 | D03 | C-NSWGA-AC2132C-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Air Cooler 2132C
229 | D03 | C-NSWGA-AC2132C-04 | - | GCS-400-NSWG-001A | - | - | 2×4 | 2C | 4 | - | - | 310 | M20 | M20 EX | 16 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | Ammeter for for Air Cooler 2132C
230 | D02 | L-NSWGE-PKC2203A1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Instrument & Plant Air Package A
231 | D02 | L-NSWGE-PKC2203A2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203A | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Instrument & Plant Air Package A
232 | D02 | L-NSWGE-PKC2203B1 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Instrument & Plant Air Package B
233 | D02 | L-NSWGE-PKC2203B2 | 0.4 | GCS-400-NSWG-001E | PK-C-2203B | 80 | 3×120+70 | 4C | 120 | 70 | - | 270 | M63 | M63 EX | 59.3 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Instrument & Plant Air Package B
234 | D03 | L-NSWGA-PK2204-1 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Nitrogen Package
235 | D03 | L-NSWGA-PK2204-2 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 75 | 3×120+70 | 4C | 120 | 70 | - | 280 | M50 | M50 | 51.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Nitrogen Package
236 | D02 | L-NSWGA-PK2201 | 0.4 | GCS-400-NSWG-001A | PK-2201 | 30 | 3×120+70 | 4C | 120 | 70 | - | HOLD | M63 | M63 | 59.3 | Z | CU/MGT/XLPE/LSFOH/LSFOH | LP Flare Package
237 | D02 | L-NSWGB-PK2207 | 0.4 | GCS-400-NSWG-001B | PK-2207 | 1.85 | 4×16 | 4C | 16 | 16 | - | 250 | M32 | M32 EX | 28.1 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Corrosion Inhibitor Package (Chemical Package)
238 | D03 | L-NSWGB-PK2101 | 0.4 | GCS-400-NSWG-001B | PK-2101 | 4.4 | 4×25 | 4C | 25 | 25 | - | 320 | M63 | M63 EX | 53.8 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Dehydration Package
239 | D01 | L-PK2101-P100A | 0.4 | PK-2101 | P-100/A | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Lean Teg Circulation Pump A
240 | D03 | C-PK2101-P100A1 | 0.23 | PK-2101 | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M32 | M32 | 33 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Lean Teg Circulation Pump A
241 | D02 | C-PK2101-P100A2 | 0.23 | PK-2101 | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Lean Teg Circulation Pump A
242 | D01 | C-PK2101-P100A3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Lean Teg Circulation Pump A
243 | D01 | L-PK2101-P100B | 0.4 | PK-2101 | P-100/B | 2.2 | 3×6 | 3C | 6 | - | - | 330 | M25 | M25 EX | 23.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Lean Teg Circulation Pump B
244 | D03 | C-PK2101-P100B1 | 0.23 | PK-2101 | IRP-DCS | - | 16×2.5 | 16C | 2.5 | - | - | 25 | M32 | M32 | 33 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Lean Teg Circulation Pump B
245 | D02 | C-PK2101-P100B2 | 0.23 | PK-2101 | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Lean Teg Circulation Pump B
246 | D01 | C-PK2101-P100B3 | 0.23 | PK-2101 | LCS | - | 10×2.5 | 10C | 2.5 | - | - | 330 | M32 | M32 EX | 29 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Lean Teg Circulation Pump B
247 | D02 | L-NSWGE-P2203A | 0.4 | GCS-400-NSWG-001E | P-2203A | 3 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Sump Pump A
248 | D03 | C-NSWGE-P2203A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Sump Pump A
249 | D02 | C-NSWGE-P2203A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Sump Pump A
250 | D02 | C-NSWGE-P2203A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Sump Pump A
251 | D02 | L-NSWGE-P2203B | 0.4 | GCS-400-NSWG-001E | P-2203B | 3 | 3×10 | 3C | 10 | - | - | 400 | M32 | M32 EX | 26.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Sump Pump B
252 | D03 | C-NSWGE-P2203B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 12×2.5 | 12C | 2.5 | - | - | 25 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Sump Pump B
253 | D02 | C-NSWGE-P2203B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Sump Pump B
254 | D02 | C-NSWGE-P2203B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M25 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Sump Pump B
255 | D03 | L-NSWGE-P-2202A | 0.4 | GCS-400-NSWG-001E | P-2202A | 9 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 EX | 28.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Closed Drain Pump A
256 | D03 | C-NSWGE-P-2202A | 0.23 | GCS-400-NSWG-001E | P-2202A | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2202A
257 | D03 | C-NSWGE-P-2202A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Closed Drain Pump A
258 | D02 | C-NSWGE-P-2202A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Closed Drain Pump A
259 | D03 | C-NSWGE-P-2202A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 410 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Closed Drain Pump A
260 | D02 | L-NSWGE-P-2202B | 0.4 | GCS-400-NSWG-001E | P-2202B | 9 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 EX | 32.4 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Closed Drain Pump B
261 | D03 | C-NSWGE-P-2202B | 0.23 | GCS-400-NSWG-001E | P-2202B | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2202B
262 | D03 | C-NSWGE-P-2202B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Closed Drain Pump B
263 | D02 | C-NSWGE-P-2202B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Closed Drain Pump B
264 | D03 | C-NSWGE-P-2202B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 410 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Closed Drain Pump B
265 | D02 | L-NSWGE-P-2101A | 0.4 | GCS-400-NSWG-001E | P-2101A | 15 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Slug Pump A
266 | D03 | C-NSWGE-P-2101A | 0.23 | GCS-400-NSWG-001E | P-2101A | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2101A
267 | D03 | C-NSWGE-P-2101A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Slug Pump A
268 | D02 | C-NSWGE-P-2101A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Slug Pump A
269 | D03 | C-NSWGE-P-2101A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 210 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Slug Pump A
270 | D02 | L-NSWGE-P-2101B | 0.4 | GCS-400-NSWG-001E | P-2101B | 15 | 3×16 | 3C | 16 | - | - | 210 | M32 | M32 EX | 28.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Slug Pump B
271 | D03 | C-NSWGE-P-2101B | 0.23 | GCS-400-NSWG-001E | P-2101B | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2101B
272 | D03 | C-NSWGE-P-2101B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Slug Pump B
273 | D02 | C-NSWGE-P-2101B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Slug Pump B
274 | D03 | C-NSWGE-P-2101B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 210 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Slug Pump B
275 | D03 | L-NSWGE-P-2302A | 0.4 | GCS-400-NSWG-001E | P-2302A | 18.5 | 3×35 | 3C | 35 | - | - | 215 | M25 | M25 | 28.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Water Jockey Pump A Panel
276 | D02 | C-NSWGE-P-2302A | 0.23 | GCS-400-NSWG-001E | LCS | - | 2×4 | 2C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Ammeter for Fire Water Jockey Pump A
277 | D02 | L-NSWGE-P-2302B | 0.4 | GCS-400-NSWG-001E | P-2302B | 18.5 | 3×35 | 3C | 35 | - | - | 215 | M25 | M25 | 26.4 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Water Jockey Pump B Panel
278 | D02 | C-NSWGE-P-2302B | 0.23 | GCS-400-NSWG-001E | LCS | - | 3×4 | 3C | 4 | 4 | 4 | 215 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | LCS for Fire Water Jockey Pump B
279 | D02 | L-NSWGB-P-2209 | 0.4 | GCS-400-NSWG-001B | P-2209 | 3 | 3×4 | 3C | 4 | - | - | 90 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Potable Water Pump
280 | D03 | C-NSWGE-P-P-2209 | 0.23 | GCS-400-NSWG-001E | P-2209 | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2209
281 | D03 | C-NSWGB-P-2209-01 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Potable Water Pump
282 | D02 | C-NSWGB-P-2209-02 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Potable Water Pump
283 | D02 | C-NSWGB-P-2209-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 90 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | LCS for Potable Water Pump
284 | D03 | L-NSWGB-P-2206 | 0.4 | GCS-400-NSWG-001E | P-2206 | 1.5 | 3×4 | 3C | 4 | - | - | 215 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Diesel Oil Pump
285 | D02 | L-NSWGE-IG-2201 | 0.23 | GCS-400-NSWG-001E | IG-2201 | 1 | 5×10 | 5C | 10 | 10 | 10 | HOLD | M25 | M25 | 22.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | LP Flare Ignition Package | HOLD
286 | D02 | L-NSWGE-P-2201A | 0.4 | GCS-400-NSWG-001E | P-2201A | 1.1 | 3×10 | 3C | 10 | - | - | 420 | M20 | M20 EX | 20.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | LP Flare K.O. Drum Pump A
287 | D03 | C-NSWGE-P-2201A-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for LP Flare K.O. Drum Pump A
288 | D02 | C-NSWGE-P-2201A-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for LP Flare K.O. Drum Pump A
289 | D03 | C-NSWGE-P-2201A-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 420 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for LP Flare K.O. Drum Pump A
290 | D02 | L-NSWGE-P-2201B | 0.4 | GCS-400-NSWG-001E | P-2201B | 1.1 | 3×10 | 3C | 10 | - | - | 420 | M20 | M20 EX | 20.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | LP Flare K.O. Drum Pump B
291 | D03 | C-NSWGE-P-2201B-01 | 0.23 | GCS-400-NSWG-001E | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for LP Flare K.O. Drum Pump B
292 | D02 | C-NSWGE-P-2201B-02 | 0.23 | GCS-400-NSWG-001E | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for LP Flare K.O. Drum Pump B
293 | D03 | C-NSWGE-P-2201B-03 | 0.23 | GCS-400-NSWG-001E | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 420 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for LP Flare K.O. Drum Pump B
294 | D02 | L-NSWGA-P-2103A | 0.4 | GCS-400-NSWG-001A | P-2103A | 5.5 | 3×16 | 3C | 16 | - | - | 370 | M25 | M25 EX | 22.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Glycol Transfer Pump A
295 | D03 | C-NSWGE-P-2103A-04 | 0.23 | GCS-400-NSWG-001E | P-2103A | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for 2103A
296 | D03 | C-NSWGA-P-2103A-01 | 0.23 | GCS-400-NSWG-001A | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-DCS for Glycol Transfer Pump A
297 | D02 | C-NSWGA-P-2103A-02 | 0.23 | GCS-400-NSWG-001A | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Glycol Transfer Pump A
298 | D03 | C-NSWGA-P-2103A-03 | 0.23 | GCS-400-NSWG-001A | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Glycol Transfer Pump A
299 | D02 | L-NSWGB-P-2103B | 0.4 | GCS-400-NSWG-001B | P-2103B | 5.5 | 3×16 | 3C | 16 | - | - | 370 | M25 | M25 EX | 22.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Glycol Transfer Pump B
300 | D03 | C-NSWGE-P-2103B-04 | 0.23 | GCS-400-NSWG-001E | P-2103B | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2103B
301 | D03 | C-NSWGB-P-2103B-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP--DCS for Glycol Transfer Pump B
302 | D02 | C-NSWGA-2103B-04 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Glycol Transfer Pump B
303 | D03 | C-NSWGB-P-2103B-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 370 | M25 | M25 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Glycol Transfer Pump B
304 | D02 | L-NSWGB-P-2102 | 0.4 | GCS-400-NSWG-001B | P-2102 | 1.1 | 3×10 | 3C | 10 | - | - | 340 | M20 | M20 EX | 20.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Glycol Manual Pump
305 | D03 | C-NSWGB-P-2102-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP--DCS & ESD for Glycol Manual Pump
306 | D02 | C-NSWGA-2102-04 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Glycol Manual Pump
307 | D03 | C-NSWGB-P-2102-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 340 | M25 | M32 EX | 29 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Glycol Manual Pump
308 | D02 | L-NSWGB-P-2104 | 0.4 | GCS-400-NSWG-001B | P-2104 | 3 | 3×10 | 3C | 10 | - | - | 400 | M20 | M20 EX | 20.7 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Glycol Drain Pump
309 | D03 | C-NSWGE-P-2104-01 | 0.23 | GCS-400-NSWG-001B | P-2104 | - | 2×4 | 2C | 4 | - | - | 410 | M20 | M20 EX | 16 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | AMMETER for P-2209
310 | D03 | C-NSWGB-P-2104-02 | 0.23 | GCS-400-NSWG-001B | IRP-DCS | - | 14×2.5 | 14C | 2.5 | - | - | 25 | M25 | M25 | 26.1 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP--DCS & ESD for Glycol Drain Pump
311 | D02 | C-NSWGA-P-2104-04 | 0.23 | GCS-400-NSWG-001B | IRP-ESD | - | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 20 | M20 | M20 | 14.2 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | IRP-ESD for Glycol Manual Pump
312 | D03 | C-NSWGB-P-2104-03 | 0.23 | GCS-400-NSWG-001B | LCS | - | 7×2.5 | 7C | 2.5 | - | - | 400 | M25 | M32 EX | 25.3 | D | Cu/PVC/Bd/Lsh/Bd/SWA/PVC - NYKYRY (CONTROL MULTI-CORE WITH LEAD SHEATH) | LCS for Glycol Drain Pump
313 | D02 | L-NSWGB-CR-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-CR-01 | 10 | 4×25 | 4C | 25 | 25 | - | 260 | M40 | M40 EX | 34.4 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Main Compressor Crane
314 | D02 | L-NSWGA-CR-02 | 0.4 | GCS-400-NSWG-001A | GCS-400-CR-02 | 5 | 4×10 | 4C | 10 | 10 | - | 200 | M25 | M25 | 22.1 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Water Pumps Crane
315 | D02 | L-NSWGB-NDP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-NDP-01 | 13.7 | 3×70+35 | 4C | 70 | 35 | - | 250 | M50 | M50 EX | 47.9 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Process Area Normal Lighting Panel
316 | D02 | L-NSWGE-EDP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-01 | 3.92 | 4×16 | 4C | 16 | 16 | - | 250 | M25 | M25 EX | 22.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Process Area Emergency Lighting Panel
317 | D02 | L-NSWGA-NDP-02 | 0.4 | GCS-400-NSWG-001A | GCS-400-NDP-02 | 6.6 | 4×35 | 4C | 35 | 35 | - | 220 | M32 | M32 | 28.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Utility Area Normal Lighting Panel
318 | D02 | L-NSWGE-EDP-02 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-02 | 3.2 | 4×16 | 4C | 16 | 16 | - | 220 | M25 | M25 | 22.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Utility Area Emergency Lighting Panel
319 | D02 | L-NSWGB-WS-PR-01 | 0.4 | GCS-400-NSWG-001B | WS-PR-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 250 | M50 | M50 EX | 42.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | First Welding Receptacle (Process Area)
320 | D01 | L-WS-PR-01-WS-PR-02 | 0.4 | WS-PR-01 | WS-PR-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 75 | M50 | M50 EX | 42.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Second Welding Receptacle (Process Area)
321 | D01 | L-WS-PR-01-SC-PR-01 | 0.23 | WS-PR-01 | SC-PR-01 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Fisrt Outlet Socket (Process Area)
322 | D01 | L-WS-PR-02-SC-PR-02 | 0.23 | WS-PR-02 | SC-PR-02 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Second Outlet Socket (Process Area)
323 | D02 | L-NSWGA-WS-PR-03 | 0.4 | GCS-400-NSWG-001A | WS-PR-03 | 35 | 3×50+25 | 4C | 50 | 25 | - | 310 | M50 | M50 EX | 42.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Third Welding Receptacle (Process Area)
324 | D01 | L-WS-PR-03-WS-PR-04 | 0.4 | WS-PR-03 | WS-PR-04 | 35 | 3×50+25 | 4C | 50 | 25 | - | 50 | M50 | M50 EX | 42.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Fourth Welding Receptacle (Process Area)
325 | D01 | L-WS-PR-03-SC-PR-03 | 0.23 | WS-PR-03 | SC-PR-03 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Third Welding Receptacle (Process Area)
326 | D01 | L-WS-PR-04-WS-PR-05 | 0.4 | WS-PR-04 | WS-PR-05 | 35 | 3×50+25 | 4C | 50 | 25 |  | 60 | M50 | M50 EX | 42.2 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Fifth Welding Receptacle (Process Area)
327 | D01 | L-WS-PR-04-SC-PR-04 | 0.23 | WS-PR-04 | SC-PR-04 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Fourth Outlet Socket (Process Area)
328 | D01 | L-WS-PR-05-WS-SC-05 | 0.23 | WS-PR-05 | SC-PR-05 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M25 | M25 EX | 22.6 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | to Junction Box for Fitfth Outlet Socket (Process Area)
329 | D02 | L-NSWGB-WS-UT-01 | 0.4 | GCS-400-NSWG-001B | WS-UT-01 | 35 | 3×50+25 | 4C | 50 | 25 | - | 225 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | First Welding Receptacle (Utility Area)
330 | D02 | L-WS-UT-01-SC-UT-01 | 0.23 | WS-UT-01 | SC-UT-01 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | to Junction Box for First Outlet Socket (Utility Area)
331 | D02 | L-NSWGA-WS-UT-02 | 0.4 | GCS-400-NSWG-001A | WS-UT-02 | 35 | 3×50+25 | 4C | 50 | 25 | - | 275 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Second Welding Receptacle (Utility Area)
332 | D02 | L-WS-UT-02-SC-UT-02 | 0.23 | WS-UT-02 | SC-UT-02 | 3 | 3×4 | 3C | 4 | 4 | 4 | 2 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | to Junction Box for Second Outlet Socket (Utility Area)
333 | D03 | L-NSWGA-CP01 | 0.4 | GCS-400-NSWG-001A | GCS-400-CP01 | 5 | 4×16 | 4C | 16 | 16 | - | 425 | M25 | M32 EX | 24.5 | A | Cu/XLPE/Bd/Lsh/Bd/SWA/PVC - N2XKYRY (LV MULTI-CORE WITH LEAD SHEATH) | Cathodic Protection Transformer Rectifier1
334 | D03 | L-NSWGA-110-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-110-CHG-001 | 20 | 4x16 | 4C | 16 | 16 | - | 25 | M25 | M25 | 24.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 110VDC Charger INCOMING 1
335 | D03 | L-110-CHG001-FB1-1 | 0.11DC | GCS-110-CHG-001 | 110-Fuse Box 1 | 7.5 | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | DC Charger Fuse Box 1 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
336 | D03 | L-110-CHG001-FB1-2 | 0.11DC | GCS-110-CHG-001 | 110-Fuse Box 1 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | DC Charger Fuse Box 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
337 | D03 | L-110CH-FB1-BAT1-1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | DC Charger Battery Bank 1 (POSITIVE)-Single core flexible cable with copper conductor & PVC insulation.
338 | D03 | L-110CH-FB1-BAT1-2 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | DC Charger Battery Bank 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
339 | D03 | L-NSWGE-110-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-110-CHG-002 | 20 | 4x16 | 4C | 16 | 16 | - | 30 | M25 | M25 | 24.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 110VDC Charger INCOMING 2
340 | D03 | L-110-CHG002-FB2-1 | 0.11DC | GCS-110-CHG-002 | 110-Fuse Box 2 | 7.5 | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 110VDC Charger Fuse Box 2 (POSITIVE)
341 | D03 | L-110-CHG002-FB2-2 | 0.11DC | GCS-110-CHG-002 | 110-Fuse Box 2 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 110VDC Charger Fuse Box 2 (NEGATIVE)
342 | D03 | L-110CH-FB2-BAT2-1 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 110VDC Charger Battery Bank 2 (POSITIVE)
343 | D03 | L-110CH-FB2-BAT2-2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | - | 1×50 | 1C | 50 | - | - | 20 | M20 | M20 | 20.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 110VDC Charger Battery Bank 2 (NEGATIVE)
344 | D01 | L-110CH-F03 | 0.11DC | GCS-110-CHG-F03 | 11 KV Existing Switchgear A | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 11 KV Existing Switchgear A
345 | D01 | L-110CH-F04 | 0.11DC | GCS-110-CHG-F04 | 11 KV Existing Switchgear B | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 11 KV Existing Switchgear B
346 | D01 | L-110CH-F05 | 0.11DC | GCS-110-CHG-F05 | 3.3 KV New Switchgear | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 3.3 KV New Switchgear
347 | D01 | L-110CH-F06 | 0.11DC | GCS-110-CHG-F06 | 0.4 KV New Existing Switchgear A | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New 0.4 KV Existing Switchgear A & Coupler
348 | D01 | L-110CH-F07 | 0.11DC | GCS-110-CHG-F07 | 0.4 KV New Existing Switchgear B | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New 0.4 KV Existing Switchgear B
349 | D01 | L-110CH-F08 | 0.11DC | GCS-110-CHG-F08 | 0.4 KV New Existing Switchgear E | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New 0.4 KV Existing Switchgear E
350 | D01 | L-110CH-F09 | 0.11DC | GCS-110-CHG-F09 | 0.4 KV New Switchgear A | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New Switchgear A & Coupler
351 | D01 | L-110CH-F10 | 0.11DC | GCS-110-CHG-F10 | 0.4 KV New Switchgear B | 0.75 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New Switchgear B
352 | D01 | L-110CH-F11 | 0.11DC | GCS-110-CHG-F11 | 0.4 KV New Switchgear E | 0.7 | 2×6 | 2C | 6 | - | - | 15 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 0.4 KV New Switchgear E
353 | D01 | L-110CH-F12 | 0.11DC | GCS-110-CHG-F12 | RCP | 0.7 | 2×6 | 2C | 6 | - | - | 40 | M20 A | M20 A | 16.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To RCP
354 | D03 | L-NSWGA-24-CHG001 | 0.4 | GCS-400-NSWG-001A | GCS-24-CHG-001 | 16.2 | 4X16 | 4C | 16 | 16 | - | 50 | M25 | M25 | 24.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 24VDC Charger INCOMING 1
355 | D03 | L-24-CHG001-FB1-1 | 0.024DC | GCS-24-CHG-001 | 24-Fuse Box 1 | 5.55 | 1x185 | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Fuse Box 1 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
356 | D03 | L-24-CHG001-FB1-2 | 0.024DC | GCS-24-CHG-001 | 24-Fuse Box 1 | - | 1x185 | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Fuse Box 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
357 | D03 | L-24-FB1-BAT1-1 | 0.024DC | 24-Fuse Box 1 | 24-Battery Bank 1 | 5.55 | 1x185 | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Battery Bank 1 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
358 | D03 | L-24-FB1-BAT1-2 | 0.024DC | 24-Fuse Box 1 | 24-Battery Bank 1 | - | 1x185 | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Battery Bank 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
359 | D03 | L-NSWGE-24-CHG002 | 0.4 | GCS-400-NSWG-001E | GCS-24-CHG-002 | 16.2 | 4X16 | 4C | 16 | 16 | - | 60 | M50 | M50 | 45.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 24VDC Charger INCOMING 2
360 | D03 | L-24-CHG002-FB2-1 | 0.024DC | GCS-24-CHG-002 | 24-Fuse Box 2 | 5.55 | 1x185 | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Fuse Box 2 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
361 | D03 | L-24-CHG002-FB2-2 | 0.024DC | GCS-24-CHG-002 | 24-Fuse Box 2 | - | 1x185 | 1C | 185 | - | - | 20 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Fuse Box 2 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
362 | D03 | L-24-FB2-BAT2-1 | 0.024DC | 24-Fuse Box 2 | 24-Battery Bank 2 | 5.55 | 1x185 | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Battery Bank 2 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
363 | D03 | L-24-FB2-BAT2-2 | 0.024DC | 24-Fuse Box 2 | 24-Battery Bank 2 | - | 1x185 | 1C | 185 | - | - | 15 | M50 | M50 | 50.5 | B | Cu/PVC/Bd/SWB/PVC - NYRY (LV SINGLE-CORE) CLASS 5 | 24VDC Charger Battery Bank 2 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
364 | D01 | L-24CH-F03 | 0.024DC | GCS-24-CHG-F03 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G System Panel
365 | D01 | L-24CH-F04 | 0.024DC | GCS-24-CHG-F04 | F&G System Panel | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G System Panel (Redundant)
366 | D01 | L-24CH-F05 | 0.024DC | GCS-24-CHG-F05 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G Marshaling Panel 1
367 | D01 | L-24CH-F06 | 0.024DC | GCS-24-CHG-F06 | F&G Marshaling Panel 1 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G System Panel 1 (Redundant)
368 | D01 | L-24CH-F07 | 0.024DC | GCS-24-CHG-F07 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G Marshaling Panel 2
369 | D01 | L-24CH-F08 | 0.024DC | GCS-24-CHG-F08 | F&G Marshaling Panel 2 | 2.7 | 2×95 | 2C | 95 | - | - | 20 | M40 | M40 | 37.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | F&G System Panel 2 (Redundant)
370 | D01 | L-24CH-F09 | 0.024DC | GCS-24-CHG-F09 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | FACP
371 | D01 | L-24CH-F10 | 0.024DC | GCS-24-CHG-F10 | FACP | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | FACP (Redundant)
372 | D01 | L-24CH-F11 | 0.024DC | GCS-24-CHG-F09 | FACP DETECTORS | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | FACP DETECTORS
373 | D01 | L-24CH-F12 | 0.024DC | GCS-24-CHG-F10 | FACP DETECTORS | 0.9 | 2×50 | 2C | 50 | - | - | 30 | M32 | M32 | 30.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | FACP DETECTORS (Redundant)
374 | D01 | L-24CH-F13 | 0.024DC | GCS-24-CHG-F11 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Protection & Total Flooding System UCP
375 | D01 | L-24CH-F14 | 0.024DC | GCS-24-CHG-F12 | Fire Protection | 0.8 | 2×120 | 2C | 120 | - | - | 80 | M50 | M50 | 41 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Protection & Total Flooding System UCP (Redundant)
376 | D03 | L-NSWGB-110-UPS001 | 0.4 | GCS-400-NSWG-001B | GCS-110-UPS-001 | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 45 | M40 | M40 | 41.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 110VAC UPS INCOMING 1
377 | D03 | L-110-UPS001-FB1-1 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 1 | 25 | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Fuse Box 1 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
378 | D03 | L-110-UPS001-FB1-2 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 1 | - | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Fuse Box 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
379 | D03 | L-110UPS-FB1-BAT1-1 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | 25 | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Battery Bank 1 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
380 | D03 | L-110UPS-FB1-BAT1-2 | 0.11DC | 110-Fuse Box 1 | 110-Battery Bank 1 | - | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Battery Bank 1 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
381 | D03 | L-NSWGA-110-UPS002 | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-002 | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 55 | M40 | M40 | 41.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 110VAC UPS INCOMING 2
382 | D03 | L-110-UPS002-FB2-1 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 2 | 25 | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Fuse Box 2 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
383 | D03 | L-110-UPS002-FB2-2 | 0.11DC | GCS-110-UPS-001 | 110-Fuse Box 2 | - | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Fuse Box 2 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
384 | D03 | L-110UPS-FB2-BAT2-1 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | 25 | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Battery Bank 2 (POSITIVE) (Single core flexible cable with copper conductor & PVC insulation.)
385 | D03 | L-110UPS-FB2-BAT2-2 | 0.11DC | 110-Fuse Box 2 | 110-Battery Bank 2 | - | 1×150 | 1C | 150 | - | - | 15 | M50 | M50 | 44.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | UPS Battery Bank 2 (NEGATIVE)-Single core flexible cable with copper conductor & PVC insulation.
386 | D02 | L-NSWGE-UPS-Bypass | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-Bypass | 43.41 | 3×70+35 | 4C | 70 | 35 | - | 55 | M40 | M40 | 41.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | 110VAC UPS By Pass
387 | D01 | L-110UPS-F03 | 0.11AC | GCS-110-UPS-F03 | DCS System Panel | 0.04 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply
388 | D01 | L-110UPS-F04 | 0.11AC | GCS-110-UPS-F04 | DCS System Panel | 0.04 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply (Redundant)
389 | D01 | L-110UPS-F05 | 0.11AC | GCS-110-UPS-F05 | DCS MARSHALLING PANEL | 0.04 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Power Supply for CPUs
390 | D01 | L-110UPS-F06 | 0.11AC | GCS-110-UPS-F06 | DCS MARSHALLING PANEL | 0.04 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Power Supply for CPUs (Redundant)
391 | D01 | L-110UPS-F07 | 0.11AC | GCS-110-UPS-F07 | DCS MARSHALLING PANEL | 0.04 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Power Supply for CPUs (Redundant)
392 | D01 | L-110UPS-F08 | 0.11AC | GCS-110-UPS-F08 | SERVER/ NETWORK | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply
393 | D01 | L-110UPS-F09 | 0.11AC | GCS-110-UPS-F09 | SERVER/ NETWORK | 0.9 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 12 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply (Redundant)
394 | D01 | L-110UPS-F10 | 0.11AC | GCS-110-UPS-F10 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Power Supply for CPUs
395 | D01 | L-110UPS-F11 | 0.11AC | GCS-110-UPS-F11 | ESD System Panel | 0.7 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Power Supply for CPUs (Redundant)
396 | D01 | L-110UPS-F12 | 0.11AC | GCS-110-UPS-F12 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply
397 | D01 | L-110UPS-F13 | 0.11AC | GCS-110-UPS-F13 | ESD Marshaling Panel | 0.58 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply (Redundant)
398 | D01 | L-110UPS-F14 | 0.11AC | GCS-110-UPS-F14 | SERVER/ NETWORK | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply
399 | D01 | L-110UPS-F15 | 0.11AC | GCS-110-UPS-F15 | SERVER/ NETWORK | 0.78 | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To 110/24 VDC Power Supply (Redundant)
400 | D01 | L-110UPS-F16 | 0.11AC | GCS-110-UPS-F16 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP A System & Marshaling
401 | D01 | L-110UPS-F17 | 0.11AC | GCS-110-UPS-F17 | Elecro Gas Compressor UCP A | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP A System & Marshaling (Redundant)
402 | D01 | L-110UPS-F18 | 0.11AC | GCS-110-UPS-F18 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP B System & Marshaling
403 | D01 | L-110UPS-F19 | 0.11AC | GCS-110-UPS-F19 | Elecro Gas Compressor UCP B | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP B System & Marshaling (Redundant)
404 | D01 | L-110UPS-F20 | 0.11AC | GCS-110-UPS-F20 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP C System & Marshaling
405 | D01 | L-110UPS-F21 | 0.11AC | GCS-110-UPS-F21 | Elecro Gas Compressor UCP C | 1.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Elecro Gas Compressor UCP C System & Marshaling (Redundant)
406 | D01 | L-110UPS-F22 | 0.11AC | GCS-110-UPS-F22 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Dehydration Package A LCP/Analyzer/BMS
407 | D01 | L-110UPS-F23 | 0.11AC | GCS-110-UPS-F23 | Dehydration Package A (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Dehydration Package A LCP/Analyzer/BMS (Redundant)
408 | D01 | L-110UPS-F24 | 0.11AC | GCS-110-UPS-F24 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Dehydration Package B LCP/Analyzer/BMS
409 | D01 | L-110UPS-F25 | 0.11AC | GCS-110-UPS-F25 | Dehydration Package B (UCP/BMS) | 3 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Dehydration Package B LCP/Analyzer/BMS (Redundant)
410 | D01 | L-110UPS-F26 | 0.11AC | GCS-110-UPS-F26 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Paging System
411 | D01 | L-110UPS-F27. | 0.11AC | GCS-110-UPS-F27 | Paging System | 1 | 3×4 | 3C | 4 | 4 | 4 | 35 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Paging System (Redundant)
412 | D01 | L-110UPS-F27 | 0.11AC | GCS-110-UPS-F27 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Compressor Local UCP A
413 | D01 | L-110UPS-F28 | 0.11AC | GCS-110-UPS-F28 | Air Compressor A | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Compressor Local UCP A (Redundant)
414 | D01 | L-110UPS-F29 | 0.11AC | GCS-110-UPS-F29 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Compressor Local UCP B
415 | D01 | L-110UPS-F30 | 0.11AC | GCS-110-UPS-F30 | Air Compressor B | 2 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Compressor Local UCP B (Redundant)
416 | D02 | L-110UPS-F31 | 0.11AC | GCS-110-UPS-F31 | Air Drayer A | 1.6 | 3×50+25+25 | 5C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Drayer A Local LCP
417 | D02 | L-110UPS-F32 | 0.11AC | GCS-110-UPS-F32 | Air Drayer A | 1.6 | 3×50+25+25 | 5C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Drayer A Local LCP (Redundant)
418 | D02 | L-110UPS-F33. | 0.11AC | GCS-110-UPS-F33 | Air Drayer B | 1.6 | 3×50+25+25 | 5C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Drayer B Local LCP
419 | D02 | L-110UPS-F34. | 0.11AC | GCS-110-UPS-F34 | Air Drayer B | 1.6 | 3×50+25+25 | 5C | 50 | 25 | 25 | 300 | M40 | M40 | 36.3 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Air Drayer B Local LCP (Redundant)
420 | D01 | L-110UPS-F33 | 0.11AC | GCS-110-UPS-F33 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Nitrogen Package Local UCP A/B
421 | D01 | L-110UPS-F34 | 0.11AC | GCS-110-UPS-F34 | Nitrogen Package | 1 | 3×4 | 3C | 4 | 4 | 4 | 15 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Nitrogen Package Local UCP A/B (Redundant)
422 | D01 | L-110UPS-F35 | 0.11AC | GCS-110-UPS-F35 | Operator WorkStation | 2.964 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Operator WorkStation (Including DCS, ESD, Package)
423 | D03 | L-110UPS-F36 | 0.11AC | GCS-110-UPS-F36 | Operator WorkStation | 2.964 | 3×10 | 3C | 10 | 10 | 10 | 35 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Operator WorkStation (Including DCS, ESD, Package)
424 | D01 | L-110UPS-F37 | 0.11AC | GCS-110-UPS-F37 | DCS Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To DCS Engineering Workstation
425 | D01 | L-110UPS-F38 | 0.11AC | GCS-110-UPS-F38 | ESD Engineering Workstation | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To ESD Engineering Workstation
426 | D01 | L-110UPS-F39 | 0.11AC | GCS-110-UPS-F39 | F&G Operator / Engineering | 0.713 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To F&G Operator / Engineering
427 | D03 | L-110UPS-F41 | 0.11AC | GCS-110-UPS-F41 | Printer A | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Operator / Engineering Printer A
428 | D03 | L-110UPS-F42 | 0.11AC | GCS-110-UPS-F42 | Printer B | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Operator / Engineering Printer B
429 | D03 | L-110UPS-F43 | 0.11AC | GCS-110-UPS-F43 | Printer C | 1.8 | 3×6 | 3C | 6 | 6 | 6 | 35 | M20 A | M20 A | 17.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | To Operator / Engineering Printer C
430 | D02 | L-NSWGE-Non UPS | 0.4 | GCS-400-NSWG-001E | GCS-400-Non UPS | 19.2 | 4×25 | 4C | 25 | 25 | - | 60 | M25 | M25 | 26.4 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Non-UPS Load for Instrument
431 | D02 | L-Non UPS-F01 | 0.23 | GCS-400-Non UPS-F01 | F01 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For DCS A (Heater, Fan, Light)
432 | D02 | L-Non UPS-F02 | 0.23 | GCS-400-Non UPS-F02 | F02 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For DCS B (Heater, Fan, Light)
433 | D02 | L-Non UPS-F03 | 0.23 | GCS-400-Non UPS-F03 | F03 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For DCS C (Heater, Fan, Light)
434 | D02 | L-Non UPS-F04 | 0.23 | GCS-400-Non UPS-F04 | F04 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For DCS D (Heater, Fan, Light,Socket))
435 | D02 | L-Non UPS-F05 | 0.23 | GCS-400-Non UPS-F05 | F05 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For ESD A (Heater, Fan, Light)
436 | D02 | L-Non UPS-F06 | 0.23 | GCS-400-Non UPS-F06 | F06 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For ESD B (Heater, Fan, Light)
437 | D02 | L-Non UPS-F07 | 0.23 | GCS-400-Non UPS-F07 | F07 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For ESD C (Heater, Fan, Light,Socket))
438 | D02 | L-Non UPS-F08 | 0.23 | GCS-400-Non UPS-F08 | F08 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For F&G A (Heater, Fan, Light)
439 | D02 | L-Non UPS-F09 | 0.23 | GCS-400-Non UPS-F09 | F09 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For F&G B (Heater, Fan, Light)
440 | D03 | L-Non UPS-F10 | 0.23 | GCS-400-Non UPS-F10 | F10 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For F&G C (Heater, Fan, Light,Socket))
441 | D02 | L-Non UPS-F11 | 0.23 | GCS-400-Non UPS-F11 | F11 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP A (Heater, Fan, Light)
442 | D02 | L-Non UPS-F12 | 0.23 | GCS-400-Non UPS-F12 | F12 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP A (Heater, Fan, Light)
443 | D02 | L-Non UPS-F13 | 0.23 | GCS-400-Non UPS-F13 | F13 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP B (Heater, Fan, Light)
444 | D02 | L-Non UPS-F14 | 0.23 | GCS-400-Non UPS-F14 | F14 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP B (Heater, Fan, Light)
445 | D02 | L-Non UPS-F15 | 0.23 | GCS-400-Non UPS-F15 | F15 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP C (Heater, Fan, Light)
446 | D03 | L-Non UPS-F16 | 0.23 | GCS-400-Non UPS-F16 | F16 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Gas Compressor UCP C (Heater, Fan, Light,Socket))
447 | D02 | L-Non UPS-F17 | 0.23 | GCS-400-Non UPS-F17 | F17 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Dehydration BMS A ( if any) (Heater, Fan, Light)
448 | D03 | L-Non UPS-F18 | 0.23 | GCS-400-Non UPS-F18 | F18 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Dehydration BMS A ( if any) (Heater, Fan, Light,Socket))
449 | D02 | L-Non UPS-F19 | 0.23 | GCS-400-Non UPS-F19 | F19 | 0.4 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Dehydration BMS B ( if any) (Heater, Socket, Fan, Light)
450 | D03 | L-Non UPS-F20 | 0.23 | GCS-400-Non UPS-F20 | F20 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 10 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Dehydration BMS B( if any) (Heater, Fan, Light,Socket))
451 | D03 | L-Non UPS-F21 | 0.23 | GCS-400-Non UPS-F21 | F21 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 75 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan, Light)
452 | D03 | L-Non UPS-F22 | 0.23 | GCS-400-Non UPS-F22 | F22 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 30 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan, Light)
453 | D03 | L-Non UPS-F23 | 0.23 | GCS-400-Non UPS-F23 | F23 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Air Compressor UCP A (Heater, Socket, Fan, Light)
454 | D03 | L-Non UPS-F24 | 0.23 | GCS-400-Non UPS-F24 | F24 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 20 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Air Compressor UCP B (Heater, Socket, Fan, Light)
455 | D03 | L-Non UPS-F25 | 0.23 | GCS-400-Non UPS-F25 | F25 | 0.9 | 3×4 | 3C | 4 | 4 | 4 | 25 | M20 A | M20 A | 16.6 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cabinet Utilities For Nitrogen package UCP(Heater, Socket, Fan, Light)
456 | D03 | L-Non UPS-F26 | 0.23 | GCS-400-Non UPS-F26 | F26 | 0.5 | 3×4 | 3C | 4 | 4 | 4 | 30 | M25 | M25 | 20.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Control Desk Sockets
457 | D02 | L-NSWGE-FDP 01 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 01 | 1 | 4×4 | 4C | 4 | 4 | - | 210 | M20 A | M20 A | 17.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Diesel Panel 01 (Electrical Main Motor)
458 | D02 | L-NSWGE-FDP 02 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 02 | 1 | 4×4 | 4C | 4 | 4 | - | 210 | M20 A | M20 A | 17.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Fire Diesel Panel 02 (Diesel Engine)
459 | D02 | L-NSWGE-SPH-01 | 0.4 | GCS-400-NSWG-001E | SPH-01 | 2 | 4×4 | 4C | 4 | 4 | - | 20 | M20 A | M20 A | 17.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Space Heater & Lighting for New LV Switchgear
460 | D02 | L-NSWGE-SPH-02 | 0.4 | GCS-400-NSWG-001E | SPH-02 | 2 | 4×4 | 4C | 4 | 4 | - | 30 | M20 A | M20 A | 17.7 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Space Heater & Lighting for MV Switchgear
461 | D03 | L-NSWGE-EDP-CRM | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-CRM | 13.5 | 4×16 | 4C | 16 | 16 | - | 75 | M32 | M32 | 28.4 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Control Room Emergency Lighting Panel
462 | D03 | L-NSWGE-HVAC-CRM1 | 0.4 | GCS-400-NSWG-001E | GCS-400-HVAC-CRM1 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 1
463 | D03 | L-NSWGE-HVAC-CRM2 | 0.4 | GCS-400-NSWG-001E | GCS-400-HVAC-CRM1 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 1
464 | D03 | L-NSWGE-HVAC-CRM3 | 0.4 | GCS-400-NSWG-001E | GCS-400-HVAC-CRM1 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 1
465 | D03 | L-NSWGE-HVAC-CRM4 | 0.4 | GCS-400-NSWG-001E | GCS-400-HVAC-CRM1 | 97.9 | 1×120 | 1C |  | 120 | - | 75 | M90 | M90 | 78.4 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Control Room Emergency Distribution Panel for HVAC 1
466 | D03 | L-NSWGB-EDP-CRM5 | 0.4 | GCS-400-NSWG-001B | GCS-400-EDP-CRM2 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 2
467 | D03 | L-NSWGB-EDP-CRM6 | 0.4 | GCS-400-NSWG-001B | GCS-400-EDP-CRM2 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 2
468 | D03 | L-NSWGB-EDP-CRM7 | 0.4 | GCS-400-NSWG-001B | GCS-400-EDP-CRM2 | 97.9 | 1×240 | 1C | 240 |  | - | 75 | M90 | M90 | 78.4 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | Control Room Emergency Distribution Panel for HVAC 2
469 | D03 | L-NSWGB-EDP-CRM8 | 0.4 | GCS-400-NSWG-001B | GCS-400-EDP-CRM2 | 97.9 | 1×120 | 1C |  | 120 | - | 75 | M90 | M90 | 78.4 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Control Room Emergency Distribution Panel for HVAC 2
470 | D03 | L-NSWGE-EDP-SWHVAC | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-SWHVAC | 46 | 3×50+25 | 5C | 50 | 25 | - | 75 | M40 | M40 | 42.2 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Switchgear Emergency Distribution Panel & HVAC
471 | D03 | L-NSWGE-EDP-WARE | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-WARE | 10.2 | 4×10 | 4C | 10 | 10 | - | 100 | M25 | M25 | 24.5 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Warehouse Emergency Distribution Panel & HVAC
472 | D02 | L-NSWGE-EHTC |  | GCS-400-NSWG-001E | EHTC | [12 empty] | Electrical Heat Tracing
473 | D03 | L-NSWGA-CAP-A-01 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 140 | 3×185 (hold) | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cable 1 of LV Switchgear A Capacitor Bank
474 | D03 | L-NSWGA-CAP-A-02 | 0.4 | GCS-400-NSWG-001A | CAP-01 | 140 | 3×185 (hold) | 3C | 185 | - | - | 35 | M63 | M63 | 56.9 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cable 2 of LV Switchgear A Capacitor Bank
475 | D01 | C-NSWGA-CAP-A |  | GCS-400-NSWG-001A | CAP-01 | - | 3×4 (hold) | 3C | - | - | - | 35 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Control Cable of LV Switchgear A Capacitor Bank
476 | D03 | L-NSWGA-CAP-B-01 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 140 | 3×185 (hold) | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cable 1 of LV Switchgear B Capacitor Bank
477 | D03 | L-NSWGA-CAP-B-02 | 0.4 | GCS-400-NSWG-001B | CAP-02 | 140 | 3×185 (hold) | 3C | 185 | - | - | 25 | M63 | M63 | 56.9 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | Cable 2 of LV Switchgear B Capacitor Bank
478 | D01 | C-NSWGA-CAP-B |  | GCS-400-NSWG-001B | CAP-02 | - | 3×4 (hold) | 3C | - | - | - | 25 | M25 | M25 | 20 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | Control Cable of LV Switchgear A Capacitor Bank
479 | D03 | L-NSWGA-DG-001A1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
480 | D03 | L-NSWGA-DG-001A2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
481 | D03 | L-NSWGA-DG-001B1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
482 | D03 | L-NSWGA-DG-001B2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
483 | D03 | L-NSWGA-DG-001C1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
484 | D03 | L-NSWGA-DG-001C2 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | 300 | - | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
485 | D03 | L-NSWGA-DG-001N1 | 0.4 | GCS-400-NSWG-001E | GCS-DG-001 | 500 | 1×300 | 1C | - | 300 | - | 30 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | to Generator Control Panel
486 | D03 | L-NSWGA-DG-001A3 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
487 | D03 | L-NSWGA-DG-001A4 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
488 | D03 | L-NSWGA-DG-001B3 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
489 | D03 | L-NSWGA-DG-001B4 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
490 | D03 | L-NSWGA-DG-001C3 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
491 | D03 | L-NSWGA-DG-001C4 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C | 300 | - | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
492 | D03 | L-NSWGA-DG-001N2 | 0.4 | GCS-DG-001 | GCS-G-001 | 500 | 1×300 | 1C |  | 300 | - | 7 | M40 | M40 | 34.2 | C | Cu/XLPE/Bd/AWA/PVC - N2XRY (LV SINGLE-CORE) | From Generator Control Panel to Generator
493 | D02 | C-NSWGA-DG-001 | 0.11DC | GCS-400-NSWG-001E | GCS-DG-001 | - | 12×2.5 (hold) | 12C | 2.5 | - | - | 30 | M25 | M25 | 24.4 | E | Cu/PVC/Bd/SWA/PVC - NYRY (CONTROL MULTI-CORE) | To / From LV Switchgear
494 | D03 | H-11SWGA-CAP-1 | 11 | GCS-11-SWG-001A | Existing MV Capacitor Bank 1 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | From New Location of Existing Capacitor Bank1 to Existing MV Cell
495 | D03 | H-11SWGB-CAP-2 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 2 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | From New Location of Existing Capacitor Bank2 to Existing MV Cell
496 | D03 | H-11SWGB-CAP-3 | 11 | GCS-11-SWG-001B | Existing MV Capacitor Bank 3 | 350 kvar | 3×95 | 3C | 95 | - | - | 35 | M90 | M90 | 79.1 | I | Cu/SC/XLPE/SC/SCT/ICWS/Bd/SWA/PVC - N2XSEYRY (MV MULTI-CORE) | From New Location of Existing Capacitor Bank3 to Existing MV Cell
497 | D03 | L-NSWGE-CCTV | 0.4 | GCS-400-NSWG-001E | CCTV Control Building | 11.7 | 4×25 | 4C | 25 | 25 | - | 200 | M63 | M63 | 53.8 | B | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | GCS CCTV Emergency Distribution Panel & HVAC
498 | D03 | C-11SWGA-NSWG-IT1 | - | GCS-11-SWG-001A | GCS-400-NSWG-001A | - | 6x2.5 | 6C | 2.5 | - | - | 40 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | INTERLOCK AND INTERTRIP BETWEEN LV IN COMING & MV UPSTREAM FEEDER
499 | D03 | C-11SWGA-NSWG-IT2 | - | GCS-11-SWG-001A | GCS-400-NSWG-001A | - | 6x2.5 | 6C | 2.5 | - | - | 40 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | INTERLOCK AND INTERTRIP BETWEEN LV IN COMING & MV UPSTREAM FEEDER
500 | D03 | C-TR01-NSWG-PR1 | - | GCS-TR-001 | GCS-400-NSWG-001A | - | 5x2.5 | 5C | 2.5 | 2.5 | 2.5 | 25 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | CABLE FROM TR. NEUTERAL TO LV INC. FOR 51G PROTECTION RELAY
501 | D03 | C-TR01-NSWG-PR2 | - | GCS-TR-002 | GCS-400-NSWG-001B | - | 5x2.5 | 5C | 2.5 | 2.5 | 2.5 | 25 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | CABLE FROM TR. NEUTERAL TO LV INC. FOR 51G PROTECTION RELAY
502 | D03 | C-TR01-NSWG-PR3 | - | GCS-TR-001 | GCS-11-SWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 40 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | CABLE FROM TR 1. MECHANICAL FAULT
503 | D03 | C-TR01-NSWG-PR4 | - | GCS-TR-002 | GCS-11-SWG-001B | - | 12×2.5 | 12C | 2.5 | - | - | 40 | - | - |  | L | Cu/XLPE/Bd/SWA/PVC - N2XRY (LV MULTI-CORE) | CABLE FROM TR. 2 MECHANICAL FAULT
Note on H64: Mohsen Fahimi: سایز کابل مجددا چک شود.
Note on G257: Mohsen Fahimi: این موتور احتمالا 11 کیلو وات میباشد.
Note on G258: Mohsen Fahimi: این موتور احتمالا 11 کیلو وات میباشد.
Note on G262: Mohsen Fahimi: این موتور احتمالا 11 کیلو وات میباشد.
Note on G281: Mohsen Fahimi: این موتور احتمالا 4 کیلو وات میباشد.
Note on G310: Mohsen Fahimi: این موتور احتمالا 4 کیلو وات میباشد.

## Lighting
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | ROUT
|  |  |  | FROM | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D01 | L-NDP01F01-FLTJB34 | 0.4 | GCS-400-NDP-01/F01 | NEW FLT-34RST-JB | 8 | 5×10 | 5C | 10 | 10 | 10 | 340 | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line
2 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 100 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
3 | D01 | L-NDP01F02-FLTJB5 | 0.4 | GCS-400-NDP-01/F02 | EXISTING FLT-5RST | 3.5 | 5×10 | 5C | 10 | 10 | 10 | 190 | M25 | M25 | 28.3 | A | To Latest Flood Lighting Tower in The Line
4 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
5 | D01 | L-NDP02F01-FLTJB35 | 0.4 | GCS-400-NDP-02/F01 | NEW FLT-35RST | 4.5 | 5×10 | 5C | 10 | 10 | 10 | 210 | M25 | M25 | 22.3 | B | To Latest Flood Lighting Tower in The Line |  | شماره صفحه: 1 از 12
6 | D02 | - | 0.23 | FLT-JB | Floodlight Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 70 | M20 A | M20 A | 15.3 | Z | From Tower JB to Terminal Box & Floodlight Fixtures
7 | D01 | L-EDP02F01-JB | 0.23 | GCS-400-EDP-02/F01 | FLT-UT-F01-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 65 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
8 | D02 | - | 0.23 | FLT-UT-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
9 | D01 | L-EDP02F02-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F02-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 170 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
10 | D02 | - | 0.23 | FLT-UT-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
11 | D01 | L-EDP02F03-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F03-JB | 0.018 | 3×6 | 3C | 6 | 6 | 6 | 180 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
12 | D02 | - | 0.23 | FLT-UT-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 5 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
13 | D01 | L-EDP02F04-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F04-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 30 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
14 | D02 | - | 0.23 | FLT-UT-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
15 | D01 | L-EDP02F05-JB | 0.23 | GCS-400-EDP-02 | FLT-UT-F05-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 60 | M20 A | M20 A | 17.5 | B | To First Fluorescent Lighting JB in The Line
16 | D02 | - | 0.23 | FLT-UT-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 80 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
17 | D01 | L-EDP01F01-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F01-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 220 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
18 | D02 | - | 0.23 | FLC-PR-F01-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
19 | D01 | L-EDP01F02-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F02-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 260 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
20 | D02 | - | 0.23 | FLC-PR-F02-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
21 | D01 | L-EDP01F03-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F03-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 290 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
22 | D02 | - | 0.23 | FLC-PR-F03-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 55 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
23 | D01 | L-EDP01F04-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F04-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 320 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
24 | D02 | - | 0.23 | FLC-PR-F04-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
25 | D01 | L-EDP01F05-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F05-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 230 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
26 | D02 | - | 0.23 | FLC-PR-F05-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
27 | D01 | L-EDP01F06-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F06-JB | 0.144 | 3×6 | 3C | 6 | 6 | 6 | 270 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
28 | D02 | - | 0.23 | FLC-PR-F06-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 65 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
29 | D01 | L-EDP01F07-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F07-JB | 0.18 | 3×6 | 3C | 6 | 6 | 6 | 320 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
30 | D02 | - | 0.23 | FLC-PR-F07-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 90 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
31 | D01 | L-EDP01F08-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F08-JB | 0.126 | 3×6 | 3C | 6 | 6 | 6 | 260 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
32 | D02 | - | 0.23 | FLC-PR-F08-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 130 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
33 | D01 | L-EDP01F09-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F09-JB | 0.108 | 3×6 | 3C | 6 | 6 | 6 | 100 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
34 | D02 | - | 0.23 | FLC-PR-F09-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 75 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings
35 | D01 | L-EDP01F10-JB | 0.23 | GCS-400-EDP-01 | FLC-PR-F10-JB | 0.036 | 3×6 | 3C | 6 | 6 | 6 | 160 | M25 | M25 | 23.5 | A | To First Fluorescent Lighting JB in The Line
36 | D02 | - | 0.23 | FLC-PR-F10-JB | Fluorescent Lighting Fixtures |  | 3×2.5 | 3C | 2.5 | 2.5 | 2.5 | 15 | M20 A | M20 A | 15.3 | L | From Fluorescent Lighting JB to Fluorescent Lightings