| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 11KV OVER HEAD LINE STUDY REPORT نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D02 |  | May. 2023 | AFC | H.Shakiba | M.Fakharian | A.M.Mohseni |  |
| D01 |  | Jul. 2022 | IFA | H.Shakiba | M.Fakharian | M.Mehrshad |  |
| D00 |  | Mar. 2022 | IFC | H.Shakiba | M.Fakharian | Sh.Ghalikar |  |
| Rev. |  | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | Client Approval |
| Class:1 |  |  | Client Doc. Number: F0Z-707423 |  |  |  |  |
| Status: |  | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X |  |  |  | 51 |  |  |  |  |  |
| 2 | X | X | X |  |  |  | 52 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 | X | X |  |  |  |  | 55 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 | X | X |  |  |  |  | 58 |  |  |  |  |  |
| 9 | X | X |  |  |  |  | 59 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 | X | X |  |  |  |  | 62 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 | X | X |  |  |  |  | 64 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  | X | X |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  | X |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

3.1	Local Codes & Standards	5

3.2	International Codes & Standards	5

3.3	The Project Documents	5

3.4	Environmental Data	5

4.0	Conductor and shield wire parameter	6

5.0	ELECTRICAL CALCULATIONS OF PHASE CONDUCTOR	6

5.1	Ampacity Calculation	6

5.2	Short Circuit Calculation	8

6.0	Electrical Parameter Calculation	8

7.0	power losses	9

8.0	INSULATOR AND FITTING CALCULATIONS	9

8.1	Arcing Distance	9

8.2	Creepage Distance	9

8.3	Mechanical Tension Rate	12

8.4	Result	12

9.0	Selection of Load condition	13

10.0	tower loading table	14

11.0	Conductor & Shield wire tension criteria	18

12.0	Tower loading table	18

13.0	Tower drawings	21

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, construction of well location, access roads, wellhead facilities for 6 new wells (with electric power supply for 2 of them) and required modifications on 4 workover wells (with electric power supply) shall be done. In addition, construction of 6 new flowlines from new wells to Binak B/C unit (with extension of relevant manifold) are in the Project scope of work.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Construction of New Well Locations, Modifications on Workover Wells, Wellhead Facilities, Electrification Facilities, Flowlines and Extension of Binak B/C Manifold |
| EPD/EPC CONTRACTOR(GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPC CONTRACTOR (GC) and approved by GC & COMPANY (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by COMPANY rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This document covers minimum necessary requirements for checking of Electrical & Mechanical parameters and study of 11KV OHL for approximately 5km (worst condition) single circuit to feeding 250kVA load in Binak Oilfield Development-BK05,12,15 and W007,046 (according to the route plan drawing and plan profile spotting).

It shall be used in conjunction with data/requisition sheets for present document subject.

- NORMATIVE REFERENCES

## Local Codes & Standards

- IPS-E-EL-100                  	Engineering Standard for Electrical System Design

- IPS-E-EL-160                  	Engineering Standard for Overhead Transmission & Distribution Lines

## International Codes & Standards

- Islamic republic of Iran vice presidency for strategic planning and supervision, General technical specification and execution procedures for transmission lines, General design of power lines, Journal No: 402

- Islamic republic of Iran vice presidency for strategic planning and supervision, General technical specification and execution procedures for cable and overhead power distribution lines, Journal No: 374

## The Project Documents

- BK-W007S-PEDCO-110-EL-DW-0001	Over Head Line Plan and Profile - W007S

- BK-W046S-PEDCO-110-EL-DW-0001	Over Head Line Plan and Profile - W046S

- BK-BK05-PEDCO-110-EL-DW-0001		Over Head Line Plan and Profile – BK05

- BK-BK12-PEDCO-110-EL-DW-0001		Over Head Line Plan and Profile - BK12

- BK-BK15-PEDCO-110-EL-DW-0001		Over Head Line Plan and Profile - BK15

- BK-SSGRL-PEDCO-110-EL-CN-0011	Calculation note for 11kv OHL Sag Tension

## Environmental Data

Refer to "Electrical System Design Criteria; Doc. No. Electrical System Design Criteria".

- Conductor and shield wire parameter

Conductor and shield wire parameters are according to below table:

| Code Name | Stranding and wire diameter |  | Overall diameter | Area |  |  | Weight | Nominal Breaking load |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Aluminum | Steel |  | Aluminum | Steel | total | Total | kgf |
|  | mm | mm | mm | mm² | mm² | mm² | kg/km |  |
| Hyena | 7/4.39 | 7/1.93 | 14.57 | 105.9 | 20.4 | 126.2 | 450 | 4090 |
| 7No.8 AWG | 7/3.26 |  | 9.78 | - | - | 58.43 | 390 | 7226 |

- ELECTRICAL CALCULATIONS OF PHASE CONDUCTOR

## Ampacity Calculation

The software used is “TL-Package” and input & output data is defined in next page.

This program is able to calculate maximum current capacity (Ampacity) of conductor in any environmental condition and also calculate maximum temperature of conductor with any desired current. This program use for selecting appropriate conductor for transmission line. This program is based on standard IEEE-738.

P=3*U*I*cosΦ=3*11*252.08*0.9=4.32 MW

- Radiated heat loss is heat losses due to heat radiation from the conductor.

- Convection heat loss is thermal losses due to the heat convective transfer from the conductor to the environment.

- Heat gain from the sun is the interest in absorbing thermal energy from the sun.

## Short Circuit Calculation

The thermal effect of short circuit current is according to below equation:

For K = 85 (for ACSR conductors), Short Circuit Calculation is according to below table:

(A=126.2 mm2)

| T (Sec) | 0.2 | 0.3 | 0.4 | 0.5 | 1 |
| --- | --- | --- | --- | --- | --- |
| Isc (kA) | 24 | 19.5 | 16.9 | 15.1 | 10.7 |

- Electrical Parameter Calculation

The software used is “TL-Package” and input & output data is defined in next.

This program is able to calculate electrical parameter such as resistance, inductance, capacitance, positive and zero sequence impedance,… and also regulation and need of compensation for transmission line.

- power losses

The following equation is used to calculate power losses:

According to the mentioned information and the resistance of the conductor and line load of about 250 kVA, the maximum power losses for the selected conductor is equal to:

- INSULATOR AND FITTING CALCULATIONS

## Arcing Distance

Minimum distance between conductor and pole and its accessories in terms of electrical calculated as follows:

Where:

V = Nominal voltage = 11 kV

## Creepage Distance

11kV overhead line is located in south of Iran and according to polluted condition on journal No.456 and below figure & too, according to IEC 60815 minimum nominal specific creepage distance is 31mm/kv but special pollution levels is 40mm/kV so:

Minimum required creepapge distance = 12 x 40 = 480 mm

# IEC 60815 :

In accordance with the above calculations we get:

| Minimum required Arcing distance | Minimum required Creepage distance |
| --- | --- |
| 136.5 (mm) | 480 (mm) |

## Mechanical Tension Rate

Insulator and String Tension rate for Maximum U.T.S of conductors:

By selecting of 70 kN insulator:

## Result

According to above calculations, insulator sets will be considered as below table:

| Suspension Insulator Set | Tension Insulator Set |
| --- | --- |
| 2*70KN (146*255mm,c.d=295mm) Porcelain/Ceramic Type | 2*70KN (146x255mm,c.d=295mm) Porcelain/Ceramic Type |

- Selection of Load condition

Selection of load condition is based on I.P.I.S (Iranian Power Industry Standard) According to below figure and tables:

Load condition refer to PLS-CADD software to be selected according to below tables:

Description          Air    Wind    Wind      Wire       Wire    Wire    Wire Ambient Weather     NESC   Wire     Wire

DensityVelocityPressure       Ice        Ice     Ice   Temp.   Temp.    Load Constant   Wind     Gust

Factor                 Thickness    Density    Load                  Factor          Height Response

(Q) (kg/m^3)                                                                               Adjust   Factor

(Pa/(m/s)^2)   (m/s)    (Pa)      (cm) (daN/dm^3) (daN/m) (deg C) (deg C)          (daN/m)  Model

------------------------------------------------------------------------------------------------------------------------

high wind        0.613 45.0001 1241.33         0          0       0     0.0               1        0   None        1

wind & ice        0.613      22 296.692       0.6     0.8956       0    -5.0    -5.0       1        0   None        1

eds        0.613               0         0          0       0    25.0    25.0       1        0   None        1

minimum temp        0.613               0         0          0       0    -5.0    -5.0       1        0   None        1

max temp        0.613               0         0          0       0    80.0    50.0       1        0   None        1

- tower loading table

The final ultimate loading tables of towers are as follows:

Suspension tower 3° (type A)

Tension tower 30° (type B)

Tension tower 90° (type C)

- Conductor & Shield wire tension criteria

Refer to weather condition & S.F on I.P.I.S (Iranian Power Industry Standard) Sag Tension for conductor calculated With PLS-CADD software according to below tables:

Weather case    Cable     % of Maximum  Maximum   Applicable Cable

condition Ultimate Tension Catenary (blank=all cables)

(daN)      (m)

-------------------------------------------------------------------

high wind 	Creep RS   50.000   0.000    0.000

wind & ice 	Creep RS   40.000   0.000    0.000

eds 		Creep RS   20.000   0.000    0.000

min temp 	Creep RS   25.000   0.000    0.000

max temp 	Creep RS   25.000   0.000    0.000

D02

- Tower loading table

Refer to weather condition & S.F on I.P.I.S (Iranian Power Industry Standard), Structure Loads Criteria for Tower Loading with PLS-CADD software according to below tables:

Row #	Description	Weather case	Cable  condition	Wind  Direction	Bisector  Wind Dir (deg)	Wire  Vert.  Load  Factor	Wire  and  Struct.  Wind  Load  Factor	Wire  Tension  Load  Factor	Struct.   Weight  Load  Factor	Struct.   Wind  Area  Factor	Struct.   Wind  Load  Model

1	high wind+	high wind	Initial RS	NA+	0.00	1.1	1.1	1.1	1.1	1.1	Wind on Face

2	high wind-	high wind	Initial RS	NA-	0.00	1.1	1.1	1.1	1.1	1.1	Wind on Face

3	min temp	min temp	Initial RS	NA+	0.00	1.1	1.1	1.1	1.1	1.1	Wind on Face

4	Broken Wire+ high wind	Load RS	NA+	0.00	1.1	1.1	1.1	1.1	1.1	Wind on Face

5	Broken Wire- high wind	Load RS	NA-	0.00	1.1	1.1	1.1	1.1	1.1	Wind on Face

Tower Loading Calculation for all tower type with TL software according to below tables. This software is able to calculate three forces on tower cross arm (including Vertical, Transversal and Longitudinal) in every loading case and with appropriate safety factors. These loading forces use to checking that loading table of towers is sufficient.

- Tower drawings

Tower single line diagram drawing shown in below: