## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0014_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1732 |  |  | Transmital Date: 28-Dec-2022
Document Title: Earthing Layout for Desalting Unit |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-EL-TR-1732 |  |  | Transmital Date: 28-Dec-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0014_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised as AFC after finalizing or minor comments on "Calculation Note For Earthing & Lightning System" and latest revision of "Architectural Drawing For CCTV Control Room- Binak DU" document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | ملاحظه خواهد شد. |  |  | Noted and Closed.
2 | Base on scope of work and supply, earthing system for CCTV control room (Less than 2 Ohm) will be calculated and shown in which document? |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | سیستم ارت موجود زیر یک اهم بوده و همچنین با توجه به کامنت کارفرما یک عدد میله ارت به همراه پیت بازبینی در نظر گرفته شده است، لذا نیاز شبکه ارت را تأمین می کند. |  |  | Noted and Closed.
3 | Earthing system in CCTV control room for Lighting panel, AC UPS, etc shall be shown in document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید. |  |  | Noted and Closed.
4 | Following notes shall be added: -All non-carrying current metallic part such as stairs, ladders, doors, windows, crain and etc shall be connected to earth system according to "BK-GNRAL-PEDCO-000-EL-DW-0002 Typical Installation Details & Notes For Earthing and Lightning Protection System". |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | نردبان موجود به سیستم ارت متصل گردید. همچنین نوت شماره 8 اضافه گردید. |  |  | Noted and Closed.
5 | Typical installation detail No. shall be added on layout base on Typical Installation Details & Notes For Earthing and Lightning Protection System. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید. |  |  | Noted and Closed.
6 | See attach file for civil comments. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید. |  |  | Noted and Closed.
7 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | ملاحظه خواهد شد. |  |  | Noted and Closed.
8 | No Comment. Note: -If any changes in prerequisite documents such as Architectural Drawing For CCTV Rack Room- Binak PU, this document shall be updated and submitted again. -Description for rod (Such as type of material and dimension) shall be added in legend. Meanwhile earth well shall be modified to earth pit and related technical characteristics such as dimension shall be added. On the other hand earth bar shall be with base plate and isolators. - Regarding lightning protection system has not been shown in this document therefore related notes to LPS to be deleted. |  | BK-SUR-ENG-ELE-01-06625 | 2023-01-08 | در صورت وجود هر گونه تغییر, این مدرک به روزرسانی خواهد شد. توضیحات مد نظر اضافه گردید. توضیحات مربوط به LPS حذف گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Sadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Jan-23 |  |  |  |  | Date: