## Cover (hidden)
Azar Oil Field Development Central Processing Facilities "EP"-TBE for Fire Water Pumps
Document No.: |  | ARCP-E270GG-ENMA-REEV-0003 | Contract No.: AP-1-92-92 |  |  | Page 1Of 7
"EP"-TBE for Fire Water Pumps
D00 | Issued for Comment |  | M.Kazemi | A.F.Hashemi | M.N.Malayeri
Rev. | Description |  | Prepared By | Checked By | Approved By | Date

## Tabulation (hidden)
Azar Oil Field Development Central Processing Facilities "EP"-TBE for Fire Water Pumps
Document No.: |  | ARCP-E270GG-ENMA-REEV-0003 |  |  |  |  | Contract No.: AP-1-92-92 |  |  |  |  | Page 2 Of 7
Tabulation Of Revised Pages
| Page | Q00 | D01 | D02 | D03 | D04 | Page | D00 | D01 | D02 | D03 | D04
| 1 | x |  |  |  |  | 36
| 2 | x |  |  |  |  | 37
| 3 | x |  |  |  |  | 38
| 4 | x |  |  |  |  | 39
| 5 | x |  |  |  |  | 40
| 6 | x |  |  |  |  | 41
| 7 | x |  |  |  |  | 42
| 8 | [5 empty] | 43
| 9 | [5 empty] | 44
| 10 | [5 empty] | 45
| 11 | [5 empty] | 46
| 12 | [5 empty] | 47
| 13 | [5 empty] | 48
| 14 | [5 empty] | 49
| 15 | [5 empty] | 50
| 16 | [5 empty] | 51
| 17 | [5 empty] | 52
| 18 | [5 empty] | 53
| 19 | [5 empty] | 54
| 20 | [5 empty] | 55
| 21 | [5 empty] | 56
| 22 | [5 empty] | 57
| 23 | [5 empty] | 58
| 24 | [5 empty] | 59
| 25 | [5 empty] | 60
| 26 | [5 empty] | 61
| 27 | [5 empty] | 62
| 28 | [5 empty] | 63
| 29 | [5 empty] | 64
| 30 | [5 empty] | 65
| 31 | [5 empty] | 66
| 32 | [5 empty] | 67
| 33 | [5 empty] | 68
| 34 | [5 empty] | 69
| 35 | [5 empty] | 70

## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE For Chemical Injection Packages
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 3
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | TB | 0008 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
TBE For Chemical Injection Packages نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | MAY.2023 |  | IFI |  |  |  | H. Adineh |  |  | M.Fakharian |  | A.M.Mohseni
D00 |  | Mar.2023 |  | IFI |  |  |  | H. Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 3 |  |  |  | CLIENT Doc. Number: F0Z-709230
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE For Chemical Injection Packages
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 3
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | TB | 0008 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | [7 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | [7 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Chemical Package
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
TBE for Chemical Injection Package
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 3 |  |  | شماره صفحه: 1 از 3
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | ME | TB | 0008 | D01
REQ. NO: |  |  |  | BIDDER NAME: |  | Kardanan Shargh Co |  |  | KSP Industrial Group |  | Green Mile Co
QUOTATION NO.: | [5 empty] | T-PS-401150-01-101-01-01 |  |  | KSP-BN-TO-TP-01-D1 |  | GMC‐2297‐OFR‐001
QUOTATION DATE: | [5 empty] | 15-02-2023 |  |  | 2023.02.22 |  | 2022-12-05
No. | DESCRIPTION |  |  | UNITS | REQ'D BY PURCHASER | MEETS REQUISITION REQUIREMENTS
[8 empty] | Status |  | Status |  | Status
1 | GENERAL
1.1 | Guarantee & Warranty as per project requirement |  |  | - | 12 month after succesfull start up or 18 month after delivery at site | A |  | YES | A | YES | A | YES
1.2 | Delivery Time |  |  | - | As per project requirement | 7 Month |  | YES | 7 Month | YES | 280 working days | YES
1.3 | Quality System Certificates |  |  |  | Required | A |  | YES | A | YES | A | YES
1.4 | Catalogues |  |  |  | Required | A |  | YES | A | YES | A | YES
1.5 | Signed and Stamped project MR's Scope of Supply & Work |  |  |  | Required | NS |  | NO | A | YES | NS | NO
1.6 | Deviation List |  |  |  | Required | A |  | YES | A | YES | A | YES
1.7 | Reference and Installation List |  |  |  | Required | A |  | YES | A | YES | A | YES
1.8 | Recommended Spare Part List for erection & Commissioning |  |  |  | Required | A |  | YES | A | YES | A | YES
1.9 | Delivery Location |  |  | - | Required | Factory, Mashhad |  | YES | Factory, Mashhad | YES | Factory, Shiraz | YES
1.10 | Special Tools List (If Required) |  |  |  | Required | A |  | YES | A | YES | A | YES
1.11 | P&ID |  |  |  | Required | A |  | YES | A | YES | A | YES
1.12 | Process Flow diagram |  |  |  | Required | NA |  | YES | NA | YES | NA | YES
1.13 | Main Equipment list |  |  |  | Required | A |  | YES | A | YES | A | YES
1.14 | Operating Manual |  |  |  | Required | A |  | YES | A | YES | A | YES
1.15 | Load List |  |  |  | Required | A |  | YES | A | YES | A | YES
1.16 | Utility Consumption List |  |  |  | Required | A |  | YES | A | YES | A | YES
1.17 | Control System Architecture Drawing |  |  |  | Required | A |  | YES | A | YES | A | YES
1.18 | Performance Curve |  |  |  | Required | A |  | YES | A | YES | A | YES
1.19 | Data Sheets for All Equipmen t Inside the Package |  |  |  | Required | A |  | YES | A | YES | A | YES
1.20 | Calculation Note For PSV Sizing |  |  |  | Required | NS |  | NO | A | YES | A | YES
1.21 | ESD Philosophy |  |  |  | Mar.2023 | A |  | YES | A | YES | A | YES
1.22 | Controller type of Package |  |  |  | Type A | A |  | YES | A | YES | A | YES
1.23 | Control Philosophy |  |  |  | Required | After P.O |  | YES | After P.O | YES | After P.O | YES
1.24 | Outline/General Lay-out Drawings |  |  |  | Required | NS |  | NO | A | YES | A | YES
1.25 | Recommended Spare Part List for 2 Years of Operation |  |  |  | Required | A |  | YES | A | YES | A | YES
2 | TANK DATA
2.1 | Material |  |  | - | Required | SS316L |  | YES | SS316L | YES | SS316L | YES
2.2 | Capacity |  |  | m3 | Required | 1.6 |  | YES | 2.5 | YES | 1 | YES
2.3 | Dimension(IDxH) |  |  | mm*mm | Required | NS |  | NO | 1535*1500 | YES | ~ 1000 x 1700 | YES
2.4 | Type |  |  | - | Cylindrical shell with Eliptical Heads | Cylindrical / Vertical |  | YES | Cylindrical Shell, with Torispherical Head | YES | Cylindrical, flat head, Eliptical buttom | YES
2.5 | Design Pressure |  |  | barg | Required | NS |  | NO | ATM + F.O.L | YES | ATM + F.O.L | YES
2.6 | Thickeness(Shell/Heads) (According to IPS) |  |  | mm | Required | 5 |  | YES | 5 | YES | 5 | YES
2.7 | P.W.H.T |  |  | - | Required | NA |  | YES | NA | YES | N.A. | YES
2.8 | Corrosion Allowance |  |  | mm | Required | 0 |  | YES | 0 | YES | 0 | YES
2.9 | Impact Test |  |  | - | Required | NA |  | YES | NA | YES | N.A. | YES
2.10 | Weight Emp. /Oper. |  |  | kg | Required | NS |  | NO | 650 / 3500 | YES | 500 / 1500 | YES
2.11 | Tank Connection |  |  | - | Required | NS |  | NO | A | YES | A | YES
2.12 | Mixer Type |  |  | - | Top Mounted, Electrical Driven | A |  | YES | A | YES | A | YES
2.13 | NDT Test |  |  | - | VT, PT, LEAK TEST | A |  | YES | A | YES | A | YES
2.14 | Sand Blast & Painting /Coating |  |  | - | Required | NA |  | YES | A | YES | N.A. | NO
2.15 | Supported by |  |  | - | Legs | A |  | YES | A | YES | A | YES
2.16 | Sub Vendors |  |  | - | Required | Kardanan Shargh Co |  | YES | KSP | YES | Green Mile Co. | YES
2.17 | Radiography Test (According to IPS) |  |  | - | Required | A |  | YES | A | YES | A | YES
3 | SKID
3.1 | Material |  |  | - | Required | NS |  | NO | CS | YES | C.S. | YES
3.2 | Dimension |  |  | m*m*m | Required | 3000x 2400x3000 mm |  | YES | Appx. 4x3x3.5 m | YES | 2300 x 2700 x 2900 mm | YES
3.3 | Profile |  |  | - | Required | NS |  | NO | H14 | YES | I Beam | YES
3.4 | Connection type with tank |  |  | - | Required | NS |  | NO | Welding to Tank Leg BasePlate | YES | Bolt & Nuts | YES
3.5 | Sub Vendors |  |  | - | Required | Kardanan Shargh Co |  | YES | KSP | YES | Green Mile Co. | YES
4 | Dosing Pump Data
4.1 | Type |  |  | - | Required | Double Diaphragm |  | YES | Double Diaphragm | YES | Double Diaphragm | YES
4.2 | QTY. |  |  | - | Required | 2+2 |  | YES | 2 + 2 | YES | 2 + 2 | YES
4.3 | Design Code |  |  | - | Required | API 675 |  | YES | API 675 | YES | API-675 | YES
4.4 | Stroke Adjustment |  |  | - | Required | Local, Manual |  | YES | Local, Manual | YES | Local, Manual | YES
4.5 | Wetted Part Material |  |  | - | Required | SS316L |  | YES | SS316L | YES | S.S. 316 | YES
4.6 | Service |  |  | - | Required | Corrosion Inhibitor |  | YES | Corrosion Inhibitor | YES | Corrosion Inhibitor | YES
4.7 | Capacity Max. |  |  | L/Hr. | Required | 3.388 |  | YES | 4 | YES | 2.3 / 3.1 | YES
4.8 | Dis. Pressure Max |  |  | Barg. | Required | 62 |  | YES | 62 & 9 | YES | 62 / 9 | YES
4.9 | Motor Power |  |  | Kw | Required | 0.75 |  | YES | 0.37 | YES | 0.37 | YES
4.10 | Ingress Protection |  |  | - | Required | IP55 |  | YES | IP55 | YES | IP 55 | YES
4.11 | Connection |  |  | Suc./Dis. | Required | 1/2" |  | YES | 1/2" RF #600 | YES | 1/2" #300 | YES
4.12 | Sub Vendors |  |  | - | Required | DEPAMU |  | YES | KSP | YES | OMG (Italy) | YES
5 | MIXER DATA
5.1 | Type |  |  | - | Required | Pitched Blade Turbine |  | YES | Vertical, Center, Top Mounted | YES | Flat | YES
5.2 | RPM |  |  | - | Required | NS |  | NO | 24 | YES | 80 | YES
5.3 | Driver |  |  |  | Required | ElectroMotor |  | YES | ElectroMotor | YES | ElectroMotor | YES
5.4 | Anti Rotation |  |  |  | Required | NS |  | NO | A | YES | NS | NO
5.5 | Gear Box Type |  |  |  | Required | NS |  | NO | Wormed Screw | YES | Worm | YES
5.6 | Manufacture |  |  |  | Required | Kardanan Shargh |  | YES | KSP | YES | Green Mile | YES
5.7 | Power |  |  | kW | Required | 0.75 |  | YES | 0.37 | YES | 0.37 | YES
5.8 | Speed(Max/Min) |  |  | rpm | Required | 1450 |  | YES | 1450 | YES | 1450 | YES
5.9 | Ratio |  |  |  | Required | NS |  |  | 1/60 | YES | 1450 : 80 | YES
5.10 | Impeller (Blade Dimension./Mat./Q.T.Y) |  |  | - | Required | NS |  | NO | 400 / S.S. / 1 | YES | 400 / S.S. / 1 | YES
5.11 | Mixer sealing type |  |  | - | Packing | Packing |  | YES | Packing | YES | N | NO
5.12 | Shaft(Mat./Lngth./Diameter./) |  |  | - | Required | SS 316L |  | YES | SS316L / 1300 mm /34 mm | YES | S.S. / 1500 / 15 | YES
6 | PACKAGE INTERCONNECTING PIPE & FITTINGS
6.1 | Material |  |  | - | Required | SS316L |  | YES | SS316L | YES | S.S. 316 | YES
6.2 | Rating |  |  | - | Required | NS |  | NO | #600 / #150 | YES | #600 / #300 | YES
6.3 | Type |  |  | - | Required | SW |  | YES | SW | YES | SW | YES
Final conclusion | [5 empty] | ACCEPTED |  |  | ACCEPTED |  | ACCEPTED
NOTES:
A:Accepted N:Not Accepted NA:Not Applicable NS:Not Specified C:Clarification Required VTS: Vendor to Specify
D01
D01