## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0012-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1023 |  |  | Transmital Date: 30-May-2022
Document Title: Calculation Note For 33 KV Over Head Line Sag and Tension |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1023 |  |  | Transmital Date: 30-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0012-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نقشه Plan و پروفیل نهایی شده می بایست ارائه و محاسبات با توجه به مسیر تأیید شده انجام گردد. |  | 1401-2294-199009 | 1401-06-06 | محاسبات با نقشه های پلان پروفیل چاه ها مطابقت دارد. همچنین در صورت نیاز و تغییر نقش های پلن و پروفیل، این مدرک مطالعاتی به روزرسانی خواهد شد.
| در مدرک مقدار Creepage Distance به میزان 40 mm/kv درج گردد و در محاسبات به دلیل افزایش طول مقره لحاظ گردد. |  | 1401-2294-199009 | 1401-06-06 | مدرک بر اساس Creepage Distance به میزان 40 به روزرسانی گردید و محاسبات در بخش 4.3 اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 12-Jun-22 |  |  |  |  | Date: