## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0012-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1023 |  |  | Transmital Date: 30-May-2022
Document Title: Calculation Note For 33 KV Over Head Line Sag and Tension |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1023 |  |  | Transmital Date: 30-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0012-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25
1 | A section entitled "selection of loading coditions" shall be added to this document and following items shall be added and specified with explainations: |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25
1-1 | Approximate location of the lines on the zoning map of the four climatic regions. |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | به بخش 4-1 اضافه گردید. |  |  | Noted&Closed.
1-2 | The table related to the loading conditions of the four climatic regions of Iran. (All of 4 tables shall be added.) |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | به بخش 4-2 اضافه گردید. |  |  | Noted&Closed.
2 | A section entitled "selection of Conductor" shall be added to the document and all technical characteristics such as Diameter of Conductor,Bare Conductor unit weight, Cross section Area of Conductor, etc with reference data shall be added and specified. |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | مشخصات درخواستی در جدول ورودی محاسبات درج شده است. (پیوست بخش 5) |  |  | Noted&Closed.
3 | The sag and tension table and result shall be explained in detail. |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | توضیحات مربوطه در بخش 4-5 اضافه گردید. |  |  | Noted&Closed.
4 | All coefficients in all pages shall be described in details such as hot and cold param(m) in sag and tension tables, etc. |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | توضیحات مربوطه در بخش های 4-3 و 4-4 اضافه گردید. |  |  | Noted&Closed.
5 | Applied software shall be specified and submitted to installation on PEDCO and NISOC PCs in order to check native files. Meanwhile native files for all mentioned reports in document shall be submitted in next revision. |  | BK-SUR-ENG-ELE-00-01828 | 2021-10-25 | فایل Native پیوست گردید. |  |  | See below item 6.
6 | See above item 5: Despite the consultant response, applied software has not been submitted. |  | BK-SUR-ENG-ELE-00-03586 | 2022-03-15 | فایل نرم افزار پیوست گردید. |  |  | Noted&Closed.
7 | There is conflict between this document and Over Head Line Plan and Profile from point of maximum span length view. It shall be rechecked and modified (If required). |  | BK-SUR-ENG-ELE-01-04682 | 2022-06-12 | اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 12-Jun-22 |  |  |  |  | Date: