## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0001-D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1702 |  |  | Transmital Date: 17-Dec-2022
Document Title: Electrical Typical Schematic Diagrams For MV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-EL-TR-1702 |  |  | Transmital Date: 17-Dec-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0001-D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحات 6/7&4:پیرو بند 2 نامه شماره 222997 مورخ 22-06-1401،حداقل سایز کابل های کنترل می بایست 2.5mm2 در نظر گرفته شود. |  | 01-2294-418921 | 1401-11-03 | سایز کابلها به 2.5 تغییر یافت.
2 | صفحه 5/7:پیرو بند 12 نامه شماره 222997 مورخ 22-06-1401،کابل RTD می بایست به صورت سه سیمه با سطح مقطع 1.5 میلی متر مربع (12T1.5) در نظر گرفته شود |  | 01-2294-418921 | 1401-11-03 | اعمال گردید.
3 | صفحه 5/7:در مدار مربوط به الکترو موتور کمپرسور گاز مسیر تست لحاظ نشده است. |  | 01-2294-418921 | 1401-11-03 | اعمال گردید.
4 | کنتاکت مربوط به لیمیت سوِئیچ شارژ فنر در مدار رله RS(ready to start)قرار داده شود. |  | 01-2294-418921 | 1401-11-03 | به صورت نوت در مدرک نشان داده شده است.
5 | پیرو بند 1-8 نامه شماره 255788 مورخ 18-07-1401،کنتاکت مربوط به TCS می بایست در هر دو وضعیت تست و سرویس قرار داده شود. |  | 01-2294-418921 | 1401-11-03 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Dec-22 |  |  |  |  | Date: