## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0011_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1863 |  |  | Transmital Date: 14-Feb-2023
Document Title: Wiring Diagram For Interposing Relay Panel (IRP) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0111-EL-TR-1863 |  |  | Transmital Date: 14-Feb-2023
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0011_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -I/O List for control system -I/O List for ESD system -Electrical I/O Signal List |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد. |  |  | Noted and Closed.
2 | Required connection between IRP and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, Diesel generator Control panel, Transformers alarm window, packages control panel, etc. shall be added to this document. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد. |  |  | Noted and Closed.
3 | Switchgear tag number of MV/LV switchgear and related terminal number shall be added to document. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد. |  |  | Noted and Closed.
4 | the cables between IRP and DCS/EDS shall be multi pair type instead of multi core. (for example 40 Pair x 1.5) |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد. |  |  | Noted and Closed.
5 | status signals will be considered Digital Input (DI) and command signals will be considered Digital Output (DO) from the DCS/ESD point of view. Therefor in order to facilitate in wiring to DI and DO cards, its proposed to considering separate multi pair cables for DI and DO signals between IRP and DCS/ESD marshaling panel. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد. |  |  | Noted and Closed.
6 | This document shall be compatible with Electrical I/O list, for example isolation command between 110V UPS/24V DC UPS and ESD has not been shown in document or start command for Closed Drain Pump A&B,Potable Water Pump,Diesel Oil Pump and LP Flare K.O. Drum Pump A&B is not applicable. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | مدرک لیست سیگنال و مدرک IRP شامل تمامی سیگنالهای مربوط به تابلوی MV، ESD و DCS مورد ویرایش قرا رگرفته است.
7 | If any changes in electrical I/O list document base on relevant comments, this document shall be revised. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | در صورت وجود هر گونه تغییر در مدارک مرتبط، این مدرک به روزرسانی خواهد شد.
8 | Final revision of this document shall be issued whenever all references document such as electrical I/O list are finalized. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | این مدرک و مدرک لیست سیگنال هر دو با هم ارسال خواهند شد.
9 | Tag number for all cables shall be mentioned in this document. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | تگ کابلهای می بایست در مدرک لیست کابل وارد شود. لذا در این مدرک که توسط ساتزنده IRP ساخته خواهد شد، نیاز به وارد نمودن تگ کابلها نمی باشد.
10 | كامنت ابزاردقيق: شماره كابل ها مشخص و در مدارك ابزار دقيق مرتبط منعكس گردد. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | تگ کابلهای می بایست در مدرک لیست کابل وارد شود. لذا در این مدرک که توسط ساتزنده IRP ساخته خواهد شد، نیاز به وارد نمودن تگ کابلها نمی باشد.
11 | كامنت ابزاردقيق: ميزان spare مناسب مطابق اسناد پيمان و Spec به ميزان 20% در نظر گرفته شود. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | اعمال گردید.
12 | كامنت ابزاردقيق: لازم به ذكر است با توجه به اينكه مدارك مرتبط نهايي نيست، مسئوليت تعداد سيگنالها از نظر مالي و زماني بر عهده پيمانكار فرعي خواهد بود. |  | BK-SUR-ENG-ELE-01-07000 | 2023-02-25 | مسئولیت هر گونه تغییر احتمالی بر عهده این پیمانکار خواهد بود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 25-Feb-23 |  |  |  |  | Date: