## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-IN-DT-0011_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1115 |  |  | Transmital Date:25 Jun 2022
Document Title: Data Sheets For Control/Regulator valves |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-T-1115 |  |  | Transmital Date:25 Jun 2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-IN-DT-0011_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | مدارک زیر به عنوان مرجع در نظر گرفته شوند: Instrument & Control System Design Criteria Spec. for Control Valves |  | 01/2294/210033 | 1401/06/13 | با توجه به نظر کارفرمای محترم ، مدرک اصلاح گردید.
2 | مشخصه Rating برای شیرهای کنترل مطابق Spec. مورد بازنگری قرار گیرد. |  | 01/2294/210033 | 1401/06/13 | با توجه به نظر کارفرمای محترم و مدارک مرجع، مدرک اصلاح گردید.
3 | سایز شیر های کنترل مورد بازنگری قرار گیرد. سایز مشخص شود و علامت X حذف گردد.(مطابق استاندارد IPS حداقل سایز شیر کنترل،یک سایز پایین تر از خط لوله میتواند در نظر گرفته شود) |  | 01/2294/210033 | 1401/06/13 | سایزینگ شیرهای کنترلی مربوط به ایستگاه تقویت فشار بر اساس توافقات صورت گرفته در ارتباط با شیرهای کنترلی بسته ی کاری منیفولد صورت گرفته است.
4 | روش سایزینگ در قالب note آورده شود. |  | 01/2294/210033 | 1401/06/13 | اعمال گردید.
5 | محاسبات سایزینگ در دیتاشیت ذکر گردد و توسط سازنده اصلاح یا تایید گردد. |  | 01/2294/210033 | 1401/06/13 | مدرک Calculation Note For Control Vale Sizing مربوط به بخش فرآیند به عنوان مرجع مدرک مذکور ذکر می گردد.
6 | پس از نهایی شده مطالعات خوردگی و مدرک PMS پروژه در خصوص متریال شیرآلات بازنگری صورت گیرد. |  | 01/2294/210033 | 1401/06/13 | مطابق آخرین نسخه مدرک PMS ، مدرک اطلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: