## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0003-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1456 |  |  | Transmital Date: 04-Oct-2022
Document Title: Calculation Note For Cable Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1456 |  |  | Transmital Date: 04-Oct-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0003-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 8.1: برای پارامتر f1 مربوط به دمای خاک دمای 35 درجه سانتی گراد لحاظ شود. |  | 1401-2294-280883 | 1401-08-03 | اعمال گردید.
2 | بند 9.2: در محاسبه مینیموم سطح مقطع کابل جریان اتصال کوتاه شبکه 50KA لحاظ شود. |  | 1401-2294-280883 | 1401-08-03 | مینیمم سطح اتصال کوتاه برای کابلهای ورودی LV پنجاه کیلوآمپر در نظر گرفته شده است. در حالیکه برای کابلهای خروجی نیاز به محاسبه مینیمم سطح مقطع کابل نمی باشد. و حذف گردید.
3 | بند 10.1: برای دمای هوا 52 درجه و دمای خاک 35 درجه سانتی گراد لحاظ شود. |  | 1401-2294-280883 | 1401-08-03 | اعمال گردید.
4 | در فایل PDF محاسابت مربوط به الکترو پمپ آب آتش نشانی ارائه نشده است. |  | 1401-2294-280883 | 1401-08-03 | اعمال گردید.
5 | در فایل اکسل attachment #1 در کاربرگ مربوط به کابل الکترو موتور 3.3KV سطح مقطع 50mm2 لحاظ شده است،در صورتی که مطابق محاسبات، مینیمم سطح مقطع برای تجهیزات MV برابر 95mm2 می باشد. |  | 1401-2294-280883 | 1401-08-03 | اعمال گردید.
6 | بدیهی است مسئولیت سایز و متراژ کابل ها بعهده ی آن پیمانکار می باشد. |  | 1401-2294-280883 | 1401-08-03 | مسئولیت سایز و متراژ کابل بر عهده این پیمانکار است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 18-Oct-22 |  |  |  |  | Date: