## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0012 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  |  | MAY.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708933
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0012 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0012 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0012 | D02
GENERAL NOTES:
1 - Zero and span adjustment shall be included and be accessible from outside in addition to HHC.
2 - Over range protection (at least 30% full scale) shall be considered.
3 - Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
4 - Painting shall be in accordance with manufacturer standard.
5 - VTA : Vendor To Advise
6 - N/A : Not Applicable
7 - Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
8 - Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.

## FT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN |  | DT | 0012 | D02
DIFF. PRESSURE TYPE FLOW TRANSMITTER
GENERAL DATA |  | 1 | Tag No. | [8 empty] | SEE NEXT PAGE
|  | 2 | P&ID No. | [8 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. / Line No. | [8 empty] | SEE NEXT PAGE
|  | 4 | Area Classification | [8 empty] | ZONE 2, IIB T4
|  | 5 | Piping Class | [8 empty] | SEE NEXT PAGE
|  | 6 | RFI Protection |  |  |  | Tropicalisation |  |  |  |  | NEEDED |  |  | Needed
OPERATING CONDITIONS |  | 7 | Fluid | [8 empty] | SEE NEXT PAGE
|  | 8 | Phase | [8 empty] | SEE NEXT PAGE
|  | 9 | Operating Pressure | [6 empty] | (Barg) |  | SEE NEXT PAGE
|  | 10 | Design Pressure | [6 empty] | (Barg) |  | SEE NEXT PAGE
|  | 11 | Operating Temperature | [6 empty] | (°C) |  | SEE NEXT PAGE
|  | 12 | Design Temperature | [6 empty] | (°C) |  | SEE NEXT PAGE
|  | 13 | Min./Normal/Max Flow Rate | [6 empty] | (Kg/h) |  | SEE NEXT PAGE
TRANSMITTER |  | 14 | Element Type | [8 empty] | SEE NEXT PAGE
|  | 15 | Size of Process Connection | [8 empty] | SEE NEXT PAGE
|  | 16 | Rating of Process Connection | [8 empty] | -
|  | 17 | Element Material | [8 empty] | SEE NEXT PAGE
|  | 18 | Enclosure Material | [8 empty] | Die cast aluminium
|  | 19 | Instrument Range | [8 empty] | SEE NEXT PAGE
|  | 20 | Power Supply | [8 empty] | 24 VDC-Loop powered
|  | 21 | Output Signal | [8 empty] | 4-20 mA
|  | 22 | Communication Protocol | [8 empty] | SMART HART (4-20mA)
|  | 23 | Electrical Connection | [8 empty] | ISO M20 x 1.5
|  | 24 | Electrical Certification | [8 empty] | EEx "ia"
|  | 25 | Ingress Protection | [8 empty] | IP-65 as minimum
|  | 26 | Accuracy |  |  |  | Write Protection |  |  |  |  | 0.1% of F.S |  |  | Not Needed (Note 1)
|  | 27 | Repetability | [8 empty] | +/- 0.1% or better
|  | 28 | Span and Zero Adjustment | [8 empty] | Required
|  | 29 | Over Range Protection | [8 empty] | SEE NEXT PAGE (1.3 of F.S)
DIAPHRAGM SEAL |  | 30 | Type | [8 empty] | N/A
|  | 31 | Size (In) | [8 empty] | N/A
|  | 32 | Fill Fluid | [8 empty] | N/A
|  | 33 | Diaphragm Material | [8 empty] | N/A
|  | 34 | Capillary Material | [8 empty] | N/A
|  | 35 | Capillary Length | [8 empty] | N/A
OPTIONS |  | 36 | Integral Indicator |  |  |  |  | Display Unit |  |  |  | Required |  |  |  | Barg
|  | 37 | Mounting Brackets | [8 empty] | Required, 2" Support Pipe
|  | 38 | Manifold |  |  |  |  | Body Material |  |  |  | SEE NEXT PAGE |  |  |  | 316 S.S.L
|  | 39 | Connection | [8 empty] | 1/2 " NPT
|  | 40 | Manifold Model |  |  |  |  | Manifold Manufacturer |  |  |  | -
|  | 41 | Integral Indicator Style | [8 empty] | LCD TYPE
|  | 42 | NACE Requirements | [8 empty] | SEE NEXT PAGE
PURCHASING DATA |  | 43 | Model |  |  |  |  | Manufacturer |  |  |  | Will be finalized later |  |  |  | Will be finalized later
|  | 44 | Supplier |  |  |  |  | Order |  |  |  | Will be finalized later |  |  |  | Will be finalized later
Notes:
(1) According to Specification For Instrumentation, If smart type transmitters are selected for ESD application they shall be configured as “write protected”. There is no Flow Transmitter for ESD.

## FT LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE FLOW TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN |  | DT |  | 0012 |  | D01
DIFF. PRESSURE TYPE FLOW TRANSMITTER LIST
Rev. | Item No. | Tag No. | P&ID No. | Equipment No. / Line No. | Service | Fluid | Connection Rating | Phase | Design Pressure (Bar-g) | Operating Pressure (Bar-g) | Design Temp. (°C) | Operating Temp. (°C) | Calibration Range (mBarg) | Instrument Range (mBarg) | Flow Rate (Kg/h) |  |  | Element Type | Element Material | Size of Process Connection (Orifice Flange Tapping) | Over Range Protection | 5-Way Valve (1/2"NPTFx1/4"NPTF ) | NACE | Model | Remark
[15 empty] | Min. | Normal | Max.
D01 MODIFIED | 1 | FIT-2101 | BK-GCS-PEDCO-120-PR-PI-0002-D06 | GAS-111-0101-AN07-6"-PT | Gas Compression Inlet Gas Pipeline (Binak) | GAS | 300# | Vapour | 18.2 | 7..5 | 85 | 46 / 26.67 | 0-250 | 0-250 | 2297.4 (Kg/hr) | 6564 (Kg/hr) | 7220.4 (Kg/hr) | Diaphragm | SS 316L | 2 x 1/2" NPTF | X 1.3 Full Scale | Yes | Yes | VTA
D01 MODIFIED | 2 | FIT-2102 | BK-GCS-PEDCO-120-PR-PI-0003-D06 | GAS-111-0001-FN07-8"-PT | Gas Compression Inlet Gas Pipeline (Golkhari) | GAS | 300# | Vapour | 41.4 | 7.5 | 85 | 32/15.5 | 0-250 | 0-250 | 3944.1605 (Kg/hr) | 11269.03 (Kg/hr) | 12395.933 (Kg/hr) | Diaphragm | SS 316L | 2 x 1/2" NPTF | X 1.3 Full Scale | Yes | Yes | VTA
D01 MODIFIED | 3 | FIT-2111 | BK-GCS-PEDCO-120-PR-PI-0004-D06 (2 of 2) | CDH-112-0014-CN05-4"-PT | Slug Catcher System | GAS | 300# | LIQUID | 23.3 | 19.5 | 85 | 15.2 | 0-250 | 0-250 | 3 (m3/h) | 10 (m3/h) | 11 (m3/h) | Diaphragm | SS 316L | 2 x 1/2" NPTF | X 1.3 Full Scale | Yes | Yes | VTA
D01 ADDED | 4 | FIT-2211 | BK-GCS-PEDCO-120-PR-PI-0016-D06 | NIT-112-0024-AN01-2"-PT | Nitrogen Package Outlet | GAS | 300# | GAS | 12.5 | 8 | 85 | 60 | 0-250 | 0-250 | 10.85 (Nm3/hr) | 31 (Nm3/hr) | 34.10 (Nm3/hr) | Diaphragm | SS 316L | 2 x 1/2" NPTF | X 1.3 Full Scale | Yes | No | VTA
D01 MODIFIED | 5 | FIT-2271 | BK-GCS-PEDCO-120-PR-PI-0022-D06 | FLG-112-0110-AN07-2"-PT | Fuel Gas System | Fuel Gas | 300# | GAS | F.V/9 | 4.9 | 85 | 48 | 0-250 | 0-250 | 177.1 (Kg/hr) | 506 (Kg/hr) | 556.6 (kg/hr) | Diaphragm | SS 316L | 2 x 1/2" NPTF | X 1.3 Full Scale | Yes | Yes | VTA
D02