## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0019 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  |  | MAY.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | A.M.Mohseni
D01 |  |  | DEC.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 | 1 |  |  |  | CLIENT Doc. Number: F9Z-708939
status: |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0019 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | X | [5 empty] | 70
7 |  | X | [6 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0019 | D02
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001
|  | Hazardous Area Classification Layout | [6 empty] | BK-GCS-PEDCO-120-SA-PY-0002
|  | Instrument & Control System Design Criteria | [6 empty] | BK-GCS-PEDCO-120-IN-DC-0002
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0019 | D02
GENERAL NOTES:
1- All transmitters shall have output short circuit & reverse polarity protection.
2- Tag plate as per Specification for Instrumentation, shall be stainless steel 304 SS (VTC). Following details shall be engraved on them:
• Tag Number • Range Limit • Service • Manufacture Model
3- Sunshade to be considered for all transmitters.
4- Each transmitter shall have a none-volatile EEprom memory to be used for storing the configuration data and sensor linearization data. This data must be retained in the transmitter to be functional upon power up.
5- Vendor shall identify and detail any deviation from the present instrument datasheet.
6- All transmitters shall be equipped with internal diagnostics software.
7- Push button for span and zero adjustment for all transmitters to be considered by vendor.
8- Indicator scale output configuration for LT tag nos. to be linear.
9- Environmental condition for field instrumentation of Binak oilfield shall be considered as per the following (According to "BK-GNRAL-PEDCO-000-PR-DB-0001: Process Basis Of Design":
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: 5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: 50 (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0

## LT-DP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | IN | DT |  | 0019 |  | D02
DATA SHEETS FOR LEVEL TRANSMITTER (DPT TYPE)
GENERAL DATA |  | 1 | Tag No. | [9 empty] | SEE PAGE 6,7
|  | 2 | P & ID No. | [9 empty] | SEE PAGE 6,7
|  | 3 | Equipment No. | [9 empty] | SEE PAGE 6,7
|  | 4 | Area Clacification | [9 empty] | Zone 2, IIB T4
|  | 5 | RFI Protection |  |  |  | Tropicalisation | [5 empty] | NEEDED |  |  |  | NEEDED
OPERATING CONDITIONS |  | 6 | Fluid | [9 empty] | SEE PAGE 6,7
|  | 7 | Phase | [9 empty] | SEE PAGE 6,7
|  | 8 | Operating Pressure |  |  |  | Design Pressure |  |  |  | (barg) |  | SEE PAGE 6,7 |  |  |  | SEE PAGE 6,7
|  | 9 | Operating Temperature |  |  |  | Design Temperature |  |  |  | (°C) |  | SEE PAGE 6,7 |  |  |  | SEE PAGE 6,7
TRANSMITTER |  | 10 | Element Type | [9 empty] | Differential Pressure
|  | 11 | Process Connection | [9 empty] | SEE PAGE 6,7
|  | 12 | Element Material | [9 empty] | SEE PAGE 6,7
|  | 13 | Enclosure Material | [9 empty] | Die-Cast Aluminium
|  | 14 | Instrument Range | [9 empty] | SEE PAGE 6,7
|  | 15 | Write Protection | [9 empty] | SEE PAGE 6,7 (Note 2)
|  | 16 | Power Supply | [9 empty] | 24 VDC-Loop powered
|  | 17 | Output Signal | [9 empty] | (4-20 mA) HART communication protocol
|  | 18 | Electrical Connection | [9 empty] | ISO M20 x 1.5
|  | 19 | Electrical Certification | [9 empty] | Eex ia -IIB T4
|  | 20 | Ingress Protection | [9 empty] | IP-65 as minimum
|  | 21 | Accuracy | [9 empty] | +/- 0.1 % Full Scale
|  | 22 | Repeatability | [9 empty] | +/- 0.1% or better
|  | 23 | Span and Zero Adjustment | [9 empty] | Required
|  | 24 | Over Range Protection | [9 empty] | 1.3 of F.S
DIAPHRAGM SEAL |  | 25 | Type | [9 empty] | N/A
|  | 26 | Size (In) | [9 empty] | N/A
|  | 27 | Fill Fluid | [9 empty] | N/A
|  | 28 | Diaphragm Material | [9 empty] | N/A
|  | 29 | Capillary Material | [9 empty] | N/A
|  | 30 | Instrument Connection | [9 empty] | N/A
|  | 31 | Capillary Length | [9 empty] | N/A
OPTIONS |  | 32 | Integral Indicator | [9 empty] | Required
|  | 33 | Mounting Brackets | [9 empty] | Required, 2" Support Pipe
|  | 34 | Manifold |  |  |  | Body Material | [5 empty] | SEE PAGE 6,7 |  |  |  | 316SS
|  | 35 | Connection | [9 empty] | N/A
|  | 36 | Manifold Model |  |  |  | Manifold Manufacturer | [5 empty] | VTA |  |  |  | VTA
|  | 37 | Local Indication Requirement | [9 empty] | Required in Digital Display, LCD type
|  | 38 | NACE Requirement |  |  |  | Manufacture | [5 empty] | SEE PAGE 6,7
PURCHASING DATA |  | 39 | Model |  |  |  | Order | [5 empty] | will be finalized later |  |  | will be finalized later
|  | 40 | Supplier |  |  |  | Manufacturer | [5 empty] | will be finalized later |  |  | will be finalized later
41
| NOTES : | VTA : VENDOR TO ADVISE
(1) Reference Document: General Specification for Instrumentation "BK-GNRAL-PEDCO-000-IN-SP-0001"
(2) The transmitters which shall be write protected are identified by note 2 in sheet 7. (Also see note 2 in sheet 7)

## LT-DP LIST
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DIFF. PRESSURE TYPE LEVEL TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 19 | D02
LEVEL TRANSMITTERS (DPT TYPE) LIST
Item No. | Tag No. | P&ID No. | Equipment No. | Fluid | Phase | Design Pressure (barg) | Operating Pressure (barg) | Design Temp. (°C) | Operating Temp. (°C) | Process Connection (Note 4) |  | Instrument Range (mm) | Element Material | Density (Kg/m3) | Nace | Diaphragm Seal & Capillary Tube Requirement | 5 WAY Manifold/(1/2" NPTx1/2'' NPT)/ TUBE Requirement | Remark
1 | LIT-2111 | BK-GCS-PEDCO-120-PR-PI-0004-D06 (1 of 2) | V-2104 | GAS | G | F.V/9 | 5.5 | 85 | (15.5 - 32) | 2 x 1/2'' NPT |  | 4000 | 316 SS | 6.2 | Yes | NO | Yes
2 | LIT-2112 (Note 2) | BK-GCS-PEDCO-120-PR-PI-0004-D06 (1 of 2) | V-2104 | GAS | G | F.V/9 | 5.5 | 85 | (15.5 - 32) | 2 x 1/2'' NPT |  | 4000 | 316 SS | 6.2 | Yes | NO | Yes
3 | LIT-2117 (Note 2) | BK-GCS-PEDCO-120-PR-PI-0005-D06 | V-2105 | GAS | G | F.V/9 | 5.3 | 85 | (19.23 - 37.17) | 2 x 1/2'' NPT |  | 1200 | 316 SS | 6.16 | Yes | NO | Yes | REV. D02 DELETED
4 | LIT-2119 | BK-GCS-PEDCO-120-PR-PI-0005-D06 | V-2105 | GAS | G | F.V/9 | 5.3 | 85 | (19.23 - 37.17) | 2 x 1/2'' NPT |  | 1200 | 316 SS | 6.16 | Yes | NO | Yes
5 | LIT-2161 (Note 2) | BK-GCS-PEDCO-120-PR-PI-0014-D06 | TK-2102 | Lean Glycol | L | FULL OF LIQUID+160mbarg/-7 | 0.1 | 85 | AMB | 2 x 1/2'' NPT |  | 3200 | 316 SS | 1100 | No | NO | Yes
6 | LIT-2162 | BK-GCS-PEDCO-120-PR-PI-0014-D06 | TK-2102 | Lean Glycol | L | FULL OF LIQUID+160mbarg/-7 | 0.1 | 85 | AMB | 2 x 1/2'' NPT |  | 3200 | 316 SS | 1100 | No | NO | Yes
7 | LIT-2221 | BK-GCS-PEDCO-120-PR-PI-0017-D06 (2 of 2) | V-2202 | Closed drain | L | F.V/7.5 | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 2400 | 316 SS | 980 | Yes | NO | Yes
8 | LIT-2251 (Note 2) | BK-GCS-PEDCO-120-PR-PI-0020-D06 (2 of 2) | V-2201 | LP Flare | L | F.V/7.5 | 0.5 | 85 | 32 | 2 x 1/2'' NPT |  | 800 | 316 SS | 980 | Yes | NO | Yes
9 | LIT-2281 | BK-GCS-PEDCO-120-PR-PI-0023-D06 | V-2206 | Diesel Oil | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 1000 | 316 SS | 850 | No | NO | Yes | REV. D02 ADDED
10 | LIT-2281A | BK-GCS-PEDCO-120-PR-PI-0023-D04 (1 of 2) | V-2206 A | Diesel Oil | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 1000 | 316 SS | 850 | No | NO | Yes | REV. D02 DELETED
11 | LIT-2281B | BK-GCS-PEDCO-120-PR-PI-0023-D04 (2 of 2) | V-2206 A | Diesel Oil | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 1300 | 316 SS | 850 | No | NO | Yes | REV. D02 DELETED
12 | LIT-2291 | BK-GCS-PEDCO-120-PR-PI-0024-D06 | TK-2209 | Potable Water | L | ATM+FULL OF WATER | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 2500 | 316 SS | 1024 | No | NO | Yes
13 | LIT-2293 | BK-GCS-PEDCO-120-PR-PI-0025-D06 | V-2107 | Glycol | L | F.V/3.5 | ATM | 85 | AMB | 2 x 1/2'' NPT |  | 1000 | 316 SS | 1100 | No | NO | Yes
14 | LIT-2301 | BK-GCS-PEDCO-120-SA-PI-0001-D06 (1 of 2) | TK-2301-A | Fire Water | L | FULL OF WATER | 1 | 85 | AMB | 2 x 1/2'' NPT |  | 11000 | 316 SS | 1000 | No | NO | Yes
15 | LIT-2302 | BK-GCS-PEDCO-120-SA-PI-0001-D06(1 of 2) | TK-2301-B | Fire Water | L | FULL OF WATER | 1 | 85 | AMB | 2 x 1/2'' NPT |  | 11000 | 316 SS | 1000 | No | NO | Yes
NOTE:
(1) G: GAS L: LIQUID
(2) Transmitters shall be of the smart transmitter type with HART communication protocol, except those connected to the ESD/HIPPS/FGS system that will be preferably of conventional electronic type. If smart type transmitters are selected for ESD application they shall be configured as “write protected”.
(3) Instrument range shall be finalized & filled by vendor.
(4) LT connection to Vessel and required accessories to be considered as per Hook up drawing.
D02