## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PR-CN-0001-V00 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: Thermal/Mechanical Calculation Books |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0003 |  |  | Transmital Date: 2024/03/09
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-PR-CN-0001_V00 |  |  | CRS Status: | CM
| Comments (PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Mechanical comments :
1 | محاسبات مربوط به plenum chamber hight ارسال گردد |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | این محاسبات بر اساس قطر فن و ابعاد باندل بوده و در نقشه های مربوطه تعیین خواهد گردید.
2 | نوع plenum مخروطی است و در محاسبات box در نظر گرفته شده . اصلاح گردد |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | مورد تایید است.
3 | داده های ورودی دما و فشار (زمستان/تابستان)با برگه اطلاعات مکانیکال مغایرت دارد. |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | این داده ها بر اساس کامنت های بخش پراسس و مدرک PFD اعمال گردیده اند.
4 | راندمان فن باید در حالت پیش فرض( 65%) در رطوبت نسبی( 100%) برای انتخاب موتور فن در نظر گرفته شود |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | مورد تایید است.
Process comments :
1 | Plot Area، در این مدرک با مدارک Datasheet ارائه شده متفاوت است. |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | احتراما ابعاد گزارش شده بر اساس HTRI و به صورت حدودی میباشد، ابعاد دقیق در مدرک GAD به حضور تقدیم خواهد گردید.
2 | تعداد Bay ها در این مدرک با تعداد Bay های درج شده در داده برگها متفاوت است. |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | احتراما در رویژن جدید اصلاح خواهد گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Al.Ahmadi P.Maleki | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 13/Dec/2023 |  |  |  |  | Date: