## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PR-DS-0002-V00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-SVTR-AA-0003 |  |  | Transmital Date:
Document Title: Process Data Sheet for AE-2102 (A/B/C) |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0003 |  |  | Transmital Date: 2024/03/09
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-PR-DS-0002-V00 |  |  | CRS Status: | CM
| Comments (PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Process comments :
1 | در سطر 6، تعداد Bay ها 1 عدد ذکر شده ولی در سطر 32 تعداد Bayها 1+2 نوشته شده که نیاز به بازنگری دارد. |  | BK-SUR-ENG-MEC-02-08884 | 2023-12-13 | احتراما در رویژن جدید اصلاح می گردد.
2 | با توجه به دمای ارائه شده در PFD سازنده کمپرسور برای Winter case، rating کولر سایز شده برای بررسی دمای خروجی در شرایط زمستان بررسی گردد. |  | BK-SUR-ENG-MEC-02-08884 | 2023-12-13 | احتراما در این شرایط با باز گذاشتن دمای خروجی سیال، این دما به 57.3 درجه خواهد رسید.
3 | Heat Duty کولر با اعداد درج شده در مدرک P&ID و داده برگ این کولر در طراحی تفصیلی متفاوت است. در این خصوص شفاف سازی گردد |  | BK-SUR-ENG-MEC-02-08884 | 13/Dec/2023 | احتراما بر اساس کامنتها (PFD)، دما ها و فشار ها تغییر داشته و با توجه به افزایش دما، دیوتی ها افزایش پیدا کرده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Maleki | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 13/Dec/2023 |  |  |  |  | Date: