| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Steel Structure Calculation Books نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| V00 | MAR. 2024 | IFA | AAC | M.FAKHARIAN | S.FRAMARZPOUR |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Status: | IFA: Issued For Approval IFI: Issued For Information AFC: Approved For Construction |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | V00 | V01 | V02 | V03 | V04 |  | PAGE | V00 | V01 | V02 | V03 | V04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 75 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 76 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 77 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 81 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 86 |  |  |  |  |  |
| 22 | X |  |  |  |  |  | 87 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 88 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 | X |  |  |  |  |  | 90 |  |  |  |  |  |
| 26 | X |  |  |  |  |  | 91 |  |  |  |  |  |
| 27 | X |  |  |  |  |  | 92 |  |  |  |  |  |
| 28 | X |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 | X |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 | X |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 | X |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 | X |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	4

3.0	Codes & Standards	4

4.0	Reference Drawing & General Document:	4

5.0	Materials	4

6.0	Descriptions of Supported Equipment:	5

7.0	EXTERNAL LOADS	5

8.0	Analyis	12

9.0	Design	13

10.0	DESIGN OUTPUT	17

11.0	BEAM CONTROL	21

12.0	Connections	22

13.0	DISPLACEMENT CONTROL	29

14.0	JOINT REACTION	31

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

- Scope

This calculation book covers a structural design for air cooler AE2101/AE2102. A 3-dimensional model analysed by means of SAP-2000 software VER. 21.0.2. This report contains computerized model, load evaluation and design verification.

- Codes & Standards

American Institute of Steel Construction.  (AISC 360-16)

Minimum Design Loads and Associated Criteria for Buildings and Other Structures (ASCE-7-10)

- Reference Drawing & General Document:

General Arrangement Drawings: (BK-GCS-AA-120-ME-DW-0001)

- Materials

- Structural Steel: S235JR (ST37)

With   Fy = 2400 kg/cm²   & Fu = 3700 kg/cm²

- Bolts: A325 (ASTM.) or equivalent HR 8.8 (DIN.) With   Fu = 8000 kg/cm²

- Anchor Bolts: ISIR/ISO 4.6 or equivalent A307 With   Fu = 4000 kg/cm²

# Descriptions of Supported Equipment:

- EXTERNAL LOADS

Load Case Definition

-Dead Load (DLs): Contain weight of steel structure & 20 percent weight of steel structure as structural connection and dead load of walk way.

-Empty Dead Load (DL): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan guard, motor, motor support, reduction system).

-Live Load (L): Live load of walkway and load due to static pressure drop of fan.

-Operation Load (EO): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan guard, motor, motor support, reduction system) and fluid weight that flows in bundles in operation.

-Test Load (ET): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan guard, motor, motor support, reduction system) and Water weight that flows in bundles in hydro test.

-ELX:  Effect of earth quake at x- direction.

-ELY:  Effect of earth quake at y- direction.

-WLX:  Effect of wind load at x- direction.

-WLY:  Effect of wind load at y- direction.

- Snow Load (SL): Snow load shall be taken as 150 kg/m2 as per site information and shall be uniformly distributed over the horizontal projection of the loaded areas.

- TL: Thermal load.

EARTHQUAKE   LOADS:

COEFFICIANT FOR SEISMIC ANALYSIS (ASCE 7-10)

| WXP | WXN |
| --- | --- |
| WYP | WYN |

Ambient Temperature ± 35°C

# Analyis

3D Computerized Model

ANALYSIS INPUT DATA

| Mass Source According ASCE7: TABLE: Masses 1 - Mass Source. Mass From; Load Pat; Multiplier. Text; Text; Unitless. Loads; DLS; 1.2. Loads; DL; 1. Loads; EO; 1. Loads; LL; 0.25. Loads; SL; 0.2. |  |
| --- | --- |

Load Pattern Definitions:

| TABLE: Load Pattern Definitions |  |  |
| --- | --- | --- |
| LoadPat | DesignType | SelfWtMult |
| Text | Text | Unitless |
| DLS | DEAD | 1.2 |
| DL | DEAD | 0 |
| EO | DEAD | 0 |
| TL | TEMPERATURE | 0 |
| LL | LIVE | 0 |
| SL | SNOW | 0 |
| WLXP | WIND | 0 |
| WLYP | WIND | 0 |
| ELX | QUAKE | 0 |
| ELY | QUAKE | 0 |
| ET | DEAD | 0 |
| WLXN | WIND | 0 |
| WLYN | WIND | 0 |

Auto Seismic - User Coefficient:

| TABLE: Auto Seismic - User Coefficient |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LoadPat | Dir | PercentEcc | EccOverride | UserZ | C | K | WeightUsed | BaseShear |
| Text | Text | Unitless | Yes/No | Yes/No | Unitless | Unitless | Kgf | Kgf |
| ELX | X | 0.05 | No | No | 0.319 | 1 | 35158.31 | 11215.5 |
| ELY | Y | 0.05 | No | No | 0.319 | 1 | 35158.31 | 11215.5 |

- Design

| TABLE: Combination Definitions |  |  |  | TABLE: Combination Definitions |  |  |  | TABLE: Combination Definitions |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ComboName | CaseName | ScaleFactor |  | ComboName | CaseName | ScaleFactor |  | ComboName | CaseName | ScaleFactor |
| Text | Text | Unitless |  | Text | Text | Unitless |  | Text | Text | Unitless |
| EM1 | DL | 1.4 |  | OP1 | DL | 1.4 |  | TE1 | DL | 1.4 |
|  | DLs | 1.4 |  |  | DLs | 1.4 |  |  | DLs | 1.4 |
|  | TL | 1.4 |  |  | TL | 1.4 |  |  | TL | 1.4 |
| EM2 | DL | 1.2 |  |  | EO | 1.4 |  |  | ET | 1.4 |
|  | DLs | 1.2 |  | OP2 | DL | 1.2 |  | TE2 | DL | 1.2 |
|  | LL | 1.6 |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  | SL | 0.5 |  |  | LL | 1.6 |  |  | LL | 1.6 |
|  | TL | 1.2 |  |  | TL | 1.2 |  |  | TL | 1.2 |
| EM3 | DL | 1.2 |  |  | EO | 1.2 |  |  | ET | 1.2 |
|  | DLs | 1.2 |  |  | SL | 0.5 |  |  | SL | 0.5 |
|  | WLXP | 1 |  | OP3 | DL | 1.2 |  | TE3 | DL | 1.2 |
|  | LL | 1 |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  | SL | 0.5 |  |  | WLXP | 1 |  |  | WLXP | 1 |
|  | TL | 1.2 |  |  | EO | 1.2 |  |  | ET | 1.2 |
| EM4 | DL | 1.2 |  |  | LL | 1 |  |  | LL | 1 |
|  | DLs | 1.2 |  |  | SL | 0.5 |  |  | SL | 0.5 |
|  | WLXN | 1 |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  | LL | 1 |  | OP4 | DL | 1.2 |  | TE4 | DL | 1.2 |
|  | SL | 0.5 |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  | TL | 1.2 |  |  | WLXN | 1 |  |  | WLXN | 1 |
| EM5 | DL | 1.2 |  |  | EO | 1.2 |  |  | ET | 1.2 |
|  | DLs | 1.2 |  |  | LL | 1 |  |  | LL | 1 |
|  | WLYP | 1 |  |  | SL | 0.5 |  |  | SL | 0.5 |
|  | LL | 1 |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  | SL | 0.5 |  | OP5 | DL | 1.2 |  | TE5 | DL | 1.2 |
|  | TL | 1.2 |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
| EM6 | DL | 1.2 |  |  | WLYP | 1 |  |  | WLYP | 1 |
|  | DLs | 1.2 |  |  | EO | 1.2 |  |  | ET | 1.2 |
|  | WLYN | 1 |  |  | LL | 1 |  |  | LL | 1 |
|  | LL | 1 |  |  | SL | 0.5 |  |  | SL | 0.5 |
|  | SL | 0.5 |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  | TL | 1.2 |  | OP6 | DL | 1.2 |  | TE6 | DL | 1.2 |
| EM7 | DL | 1.37 |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  | DLs | 1.37 |  |  | WLYN | 1 |  |  | WLYN | 1 |
|  | ELX | 1 |  |  | EO | 1.2 |  |  | ET | 1.2 |
|  | ELY | 0.3 |  |  | LL | 1 |  |  | LL | 1 |
|  | LL | 1 |  |  | SL | 0.5 |  |  | SL | 0.5 |
|  | SL | 0.2 |  |  | TL | 1.2 |  |  | TL | 1.2 |
| EM8 | DL | 1.37 |  | OP7 | DL | 1.37 |  | TE7 | DL | 1.37 |
|  | DLs | 1.37 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | ELX | 1 |  |  | ELX | 1 |  |  | ELX | 1 |
|  | ELY | -0.3 |  |  | ELY | 0.3 |  |  | ELY | 0.3 |
|  | LL | 1 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | SL | 0.2 |  |  | LL | 1 |  |  | LL | 1 |
| EM9 | DL | 1.37 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | DLs | 1.37 |  | OP8 | DL | 1.37 |  | TE8 | DL | 1.37 |
|  | ELX | -1 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | ELY | 0.3 |  |  | ELX | 1 |  |  | ELX | 1 |
|  | LL | 1 |  |  | ELY | -0.3 |  |  | ELY | -0.3 |
|  | SL | 0.2 |  |  | EO | 1.37 |  |  | ET | 1.37 |
| EM10 | DL | 1.37 |  |  | LL | 1 |  |  | LL | 1 |
|  | DLs | 1.37 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | ELX | -1 |  | OP9 | DL | 1.37 |  | TE9 | DL | 1.37 |
|  | ELY | -0.3 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | LL | 1 |  |  | ELX | -1 |  |  | ELX | -1 |
|  | SL | 0.2 |  |  | ELY | 0.3 |  |  | ELY | 0.3 |
| EM11 | DL | 1.37 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | DLs | 1.37 |  |  | LL | 1 |  |  | LL | 1 |
|  | ELY | 1 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | ELX | 0.3 |  | OP10 | DL | 1.37 |  | TE10 | DL | 1.37 |
|  | LL | 1 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | SL | 0.2 |  |  | ELX | -1 |  |  | ELX | -1 |
| EM12 | DL | 1.37 |  |  | ELY | -0.3 |  |  | ELY | -0.3 |
|  | DLs | 1.37 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | ELY | 1 |  |  | LL | 1 |  |  | LL | 1 |
|  | ELX | -0.3 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | LL | 1 |  | OP11 | DL | 1.37 |  | TE11 | DL | 1.37 |
|  | SL | 0.2 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
| EM13 | DL | 1.37 |  |  | ELY | 1 |  |  | ELY | 1 |
|  | DLs | 1.37 |  |  | ELX | 0.3 |  |  | ELX | 0.3 |
|  | ELY | -1 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | ELX | 0.3 |  |  | LL | 1 |  |  | LL | 1 |
|  | LL | 1 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | SL | 0.2 |  | OP12 | DL | 1.37 |  | TE12 | DL | 1.37 |
| EM14 | DL | 1.37 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | DLs | 1.37 |  |  | ELY | 1 |  |  | ELY | 1 |
|  | ELY | -1 |  |  | ELX | -0.3 |  |  | ELX | -0.3 |
|  | ELX | -0.3 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | LL | 1 |  |  | LL | 1 |  |  | LL | 1 |
|  | SL | 0.2 |  |  | SL | 0.2 |  |  | SL | 0.2 |
| EM15 | DL | 0.9 |  | OP13 | DL | 1.37 |  | TE13 | DL | 1.37 |
|  | DLs | 0.9 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | WLXP | 1 |  |  | ELY | -1 |  |  | ELY | -1 |
|  | TL | 1 |  |  | ELX | 0.3 |  |  | ELX | 0.3 |
| EM16 | DL | 0.9 |  |  | EO | 1.37 |  |  | ET | 1.37 |
|  | DLs | 0.9 |  |  | LL | 1 |  |  | LL | 1 |
|  | WLXN | 1 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | TL | 1 |  | OP14 | DL | 1.37 |  | TE14 | DL | 1.37 |
| EM17 | DL | 0.9 |  |  | DLs | 1.37 |  |  | DLs | 1.37 |
|  | DLs | 0.9 |  |  | ELY | -1 |  |  | ELY | -1 |
|  | WLYP | 1 |  |  | ELX | 0.3 |  |  | ELX | -0.3 |
|  | TL | 1 |  |  | EO | 1.37 |  |  | ET | 1.37 |
| EM18 | DL | 0.9 |  |  | LL | 1 |  |  | LL | 1 |
|  | DLs | 0.9 |  |  | SL | 0.2 |  |  | SL | 0.2 |
|  | WLYN | 1 |  | OP15 | DL | 0.9 |  | TE15 | DL | 0.9 |
|  | TL | 1 |  |  | DLs | 0.9 |  |  | DLs | 0.9 |
| EM19 | DL | 0.73 |  |  | WLXP | 1 |  |  | WLXP | 1 |
|  | DLs | 0.73 |  |  | EO | 0.9 |  |  | ET | 0.9 |
|  | ELX | 1 |  |  | TL | 1 |  |  | TL | 1 |
|  | ELY | 0.3 |  | OP16 | DL | 0.9 |  | TE16 | DL | 0.9 |
| EM20 | DL | 0.73 |  |  | DLs | 0.9 |  |  | DLs | 0.9 |
|  | DLs | 0.73 |  |  | WLXN | 1 |  |  | WLXN | 1 |
|  | ELX | 1 |  |  | EO | 0.9 |  |  | ET | 0.9 |
|  | ELY | -0.3 |  |  | TL | 1 |  |  | TL | 1 |
| EM21 | DL | 0.73 |  | OP17 | DL | 0.9 |  | TE17 | DL | 0.9 |
|  | DLs | 0.73 |  |  | DLs | 0.9 |  |  | DLs | 0.9 |
|  | ELX | -1 |  |  | WLYP | 1 |  |  | WLYP | 1 |
|  | ELY | 0.3 |  |  | EO | 0.9 |  |  | ET | 0.9 |
| EM22 | DL | 0.73 |  |  | TL | 1 |  |  | TL | 1 |
|  | DLs | 0.73 |  | OP18 | DL | 0.9 |  | TE18 | DL | 0.9 |
|  | ELX | -1 |  |  | DLs | 0.9 |  |  | DLs | 0.9 |
|  | ELY | -0.3 |  |  | WLYN | 1 |  |  | WLYN | 1 |
| EM23 | DL | 0.73 |  |  | EO | 0.9 |  |  | ET | 0.9 |
|  | DLs | 0.73 |  |  | TL | 1 |  |  | TL | 1 |
|  | ELX | 0.3 |  | OP19 | DL | 0.73 |  | TE19 | DL | 0.73 |
|  | ELY | 1 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
| EM24 | DL | 0.73 |  |  | ELX | 1 |  |  | ELX | 1 |
|  | DLs | 0.73 |  |  | ELY | 0.3 |  |  | ELY | 0.3 |
|  | ELX | 0.3 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | ELY | -1 |  | OP20 | DL | 0.73 |  | TE20 | DL | 0.73 |
| EM25 | DL | 0.73 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | DLs | 0.73 |  |  | ELX | 1 |  |  | ELX | 1 |
|  | ELX | -0.3 |  |  | ELY | -0.3 |  |  | ELY | -0.3 |
|  | ELY | 1 |  |  | EO | 0.73 |  |  | ET | 0.73 |
| EM26 | DL | 0.73 |  | OP21 | DL | 0.73 |  | TE21 | DL | 0.73 |
|  | DLs | 0.73 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | ELX | -0.3 |  |  | ELX | -1 |  |  | ELX | -1 |
|  | ELY | -1 |  |  | ELY | 0.3 |  |  | ELY | 0.3 |
| EM27 | DL | 1.2 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | DLs | 1.2 |  | OP22 | DL | 0.73 |  | TE22 | DL | 0.73 |
|  | SL | 1.6 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | TL | 1.2 |  |  | ELX | -1 |  |  | ELX | -1 |
|  | LL | 1 |  |  | ELY | -0.3 |  |  | ELY | -0.3 |
| EM28 | DL | 1.2 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | DLs | 1.2 |  | OP23 | DL | 0.73 |  | TE23 | DL | 0.73 |
|  | WLXN | 0.5 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | SL | 1.6 |  |  | ELX | 0.3 |  |  | ELX | 0.3 |
|  | TL | 1.2 |  |  | ELY | 1 |  |  | ELY | 1 |
| EM29 | DL | 1.2 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | DLs | 1.2 |  | OP24 | DL | 0.73 |  | TE24 | DL | 0.73 |
|  | WLXP | 0.5 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | SL | 1.6 |  |  | ELX | 0.3 |  |  | ELX | 0.3 |
|  | TL | 1.2 |  |  | ELY | -1 |  |  | ELY | -1 |
| EM30 | DL | 1.2 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | DLs | 1.2 |  | OP25 | DL | 0.73 |  | TE25 | DL | 0.73 |
|  | WLYP | 0.5 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | SL | 1.6 |  |  | ELX | -0.3 |  |  | ELX | -0.3 |
|  | TL | 1.2 |  |  | ELY | 1 |  |  | ELY | 1 |
| EM31 | DL | 1.2 |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  | DLs | 1.2 |  | OP26 | DL | 0.73 |  | TE26 | DL | 0.73 |
|  | WLYN | 0.5 |  |  | DLs | 0.73 |  |  | DLs | 0.73 |
|  | SL | 1.6 |  |  | ELX | -0.3 |  |  | ELX | -0.3 |
|  | TL | 1.2 |  |  | ELY | -1 |  |  | ELY | -1 |
|  |  |  |  |  | EO | 0.73 |  |  | ET | 0.73 |
|  |  |  |  | OP27 | DL | 1.2 |  | TE27 | DL | 1.2 |
|  |  |  |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  |  |  |  |  | LL | 1 |  |  | ET | 1.2 |
|  |  |  |  |  | SL | 1.6 |  |  | LL | 1 |
|  |  |  |  |  | TL | 1.2 |  |  | SL | 1.6 |
|  |  |  |  |  | EO | 1.2 |  |  | TL | 1.2 |
|  |  |  |  | OP28 | DL | 1.2 |  | TE28 | DL | 1.2 |
|  |  |  |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  |  |  |  |  | WLXP | 0.5 |  |  | ET | 1.2 |
|  |  |  |  |  | EO | 1.2 |  |  | WLXN | 0.5 |
|  |  |  |  |  | SL | 1.6 |  |  | SL | 1.6 |
|  |  |  |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  |  |  |  | OP29 | DL | 1.2 |  | TE29 | DL | 1.2 |
|  |  |  |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  |  |  |  |  | WLXN | 0.5 |  |  | ET | 1.2 |
|  |  |  |  |  | EO | 1.2 |  |  | WLXP | 0.5 |
|  |  |  |  |  | SL | 1.6 |  |  | SL | 1.6 |
|  |  |  |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  |  |  |  | OP30 | DL | 1.2 |  | TE30 | DL | 1.2 |
|  |  |  |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  |  |  |  |  | WLYP | 0.5 |  |  | ET | 1.2 |
|  |  |  |  |  | EO | 1.2 |  |  | WLYN | 0.5 |
|  |  |  |  |  | SL | 1.6 |  |  | SL | 1.6 |
|  |  |  |  |  | TL | 1.2 |  |  | TL | 1.2 |
|  |  |  |  | OP31 | DL | 1.2 |  | TE31 | DL | 1.2 |
|  |  |  |  |  | DLs | 1.2 |  |  | DLs | 1.2 |
|  |  |  |  |  | WLYN | 0.5 |  |  | ET | 1.2 |
|  |  |  |  |  | EO | 1.2 |  |  | WLYP | 0.5 |
|  |  |  |  |  | SL | 1.6 |  |  | SL | 1.6 |
|  |  |  |  |  | TL | 1.2 |  |  | TL | 1.2 |

- DESIGN OUTPUT

These results are related to model: 17208-AE-2101&2102-REV0

ELV. ON AXIS” A”

ELV. ON AXIS” B”

ELV. ON AXIS” 1”

ELV. ON AXIS” 2”

PLAN AT EL.: 4570

PLAN AT EL.: 5500

- BEAM CONTROL

Where chevron braces intersect a beam from below, i.e., inverted V brace, the beam shall be capable of supporting all tributary gravity loads presuming the bracing not to exist.

These results are related to model: 17208-AE-2101&2102-Unbraced-REV0

PLAN AT EL.: 5500

- Connections

COLUMN BASE PLATE AND SETTING BOLT DESIGN -These loads are related to model:  17208-AE-2101&2102-Connection-REV0 (SEISMIC COEFFICIANT Cx =0.638, Cy = 0.638)

# DISPLACEMENT CONTROL

Allowable Deflections:

Design deflection of structural steel members shall not exceed the following values:

Floor beams supporting equipment: L/450

Floor beams without equipment: L/240

Frames (horizontal):

Drift = DPL = I*DP = I*(δx- δy)= I*( δxe *Cd / I) = δxe *Cd  ≤ 0.02 H  ⇒ δxe  ≤  0.0057H

In which:

L= span of the beam; H= Height of the frame.

MODEL NAME: 17208-AE-2101&2102-REV0

SWAY OF STRUCTURE:

Max sway of structure due to Ex (in joint 6): 0.2 cm

H=550cm:     0.0057H=3.135 cm > 0.2 cm    ok.

Max sway of structure due to Ey: (in joint 13): 0.7 cm

H=550cm:     0.0057H=3.135 cm > 0.7cm    ok.

| TABLE: Joint Displacements |  |  |  |
| --- | --- | --- | --- |
| Joint | OutputCase | U1 | U2 |
| Text | Text | m | m |
| 6 | ELX | 0.2 | 0.0 |
| 6 | ELY | 0.0 | 0.3 |
| 8 | ELX | 0.2 | 0.0 |
| 8 | ELY | 0.0 | 0.3 |
| 10 | ELX | 0.2 | 0.0 |
| 10 | ELY | 0.0 | 0.3 |
| 12 | ELX | 0.2 | 0.0 |
| 12 | ELY | 0.0 | 0.3 |
| 13 | ELX | 0.2 | 0.0 |
| 13 | ELY | 0.0 | 0.7 |
| 50 | ELX | 0.2 | 0.0 |
| 50 | ELY | 0.0 | 0.7 |

CHECKING P-DELTA

Control θi:

θi=PuΔeuVuh

Δeu= 0.7

θi= 21239.49*0.76775.4*550=0.004<0.1

P-Δ need not be considered

# JOINT REACTION

| TABLE: Joint Reactions |  |  |  |  |
| --- | --- | --- | --- | --- |
| Joint | OutputCase | F1 | F2 | F3 |
| Text | Text | Kgf | Kgf | Kgf |
| A1 | DL | 817 | 322 | 5426 |
|  | EO | 33 | 14 | 160 |
|  | TL | 42 | 24 | 0 |
|  | LL | -119 | -101 | 3019 |
|  | SL | 5 | -9 | 494 |
|  | WLXP | -302 | 0 | -715 |
|  | WLYP | 0 | -769 | -2318 |
|  | ELX | -2967 | 48 | -6277 |
|  | ELY | 9 | -2828 | -7896 |
|  | DLs | 289 | 104 | 3294 |
|  | ET | 53 | 25 | 255 |
|  | WLXN | 302 | 0 | 715 |
|  | WLYN | 0 | 577 | 1738 |
| A2 | DL | -817 | 322 | 5404 |
|  | EO | -33 | 14 | 160 |
|  | TL | -42 | 24 | 0 |
|  | LL | 118 | -98 | 2909 |
|  | SL | -5 | -9 | 479 |
|  | WLXP | -302 | 0 | 715 |
|  | WLYP | 0 | -769 | -2318 |
|  | ELX | -2968 | -48 | 6277 |
|  | ELY | 4 | -2822 | -7907 |
|  | DLs | -289 | 105 | 3277 |
|  | ET | -53 | 25 | 255 |
|  | WLXN | 302 | 0 | -715 |
|  | WLYN | 0 | 577 | 1738 |
| B1 | DL | 798 | -322 | 4835 |
|  | EO | 25 | -14 | 120 |
|  | TL | 35 | -24 | 0 |
|  | LL | -133 | 101 | 449 |
|  | SL | 3 | 9 | 159 |
|  | WLXP | -302 | 0 | -714 |
|  | WLYP | 0 | -769 | 2318 |
|  | ELX | -2640 | 81 | -6127 |
|  | ELY | -29 | -2784 | 7896 |
|  | DLs | 283 | -104 | 2962 |
|  | ET | 52 | -25 | 253 |
|  | WLXN | 302 | 0 | 714 |
|  | WLYN | 0 | 577 | -1738 |
| B2 | DL | -798 | -322 | 4829 |
|  | EO | -25 | -14 | 120 |
|  | TL | -35 | -24 | 0 |
|  | LL | 134 | 98 | 418 |
|  | SL | -3 | 9 | 155 |
|  | WLXP | -302 | 0 | 714 |
|  | WLYP | 0 | -769 | 2318 |
|  | ELX | -2640 | -81 | 6127 |
|  | ELY | 16 | -2782 | 7907 |
|  | DLs | -283 | -105 | 2953 |
|  | ET | -52 | -25 | 253 |
|  | WLXN | 302 | 0 | -714 |
|  | WLYN | 0 | 577 | -1738 |