## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PM-LI-0001-V01 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title:Vendor Print Index & Schedule (VPIS) |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0012 |  |  | Transmital Date: 2024/07/09
[5 empty] | CRS No: NISOC-CRS-BK-GCS-AA-120-PM-LI-0001_V01 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Process comments :
4- |  |  | 03/2294/86986 | 1403/03/06 | 1- با توجه به اینکه پکیج کولر هوایی دراین پروژه سیستم کنترل مستقل نداشته وادوات حفاظت و اندازه گیری و تنها لوپ کنترلی آن که مربوط به کنترل زاویه پره هاست توسط سیستم DCS/ESD ایستگاه مدیریت میشود، فلسفه کنترل برای این پکیج نیاز نیست و عملکرد آن درمدرک تهیه شده توسط پیمانکار برای ایستگاه دیده شده است. برای اطمینان خاطرکارفرمای محترم توضیحات مربوط به ارتباط ادوات کنترلی با سیستم ایستگاه به عنوان نوت در مدرک P&ID آورده خواهدشد.
2- با توجه به طراحی توامان Thermal و Mechanical با نرم افزار HTRI، این مدرک بدین صورت ارائه میگردد.
3- ادوات اندازه گیری فشار و دما در خارج ازپکیج کولر هوایی قرار دارد و فقط سنسور لرزش توسط سازنده تامین میشود.
4- لطفا رجوع شود به پاسخ ارائه شده در بند 1.
5-نقطه نظر کارفرمای اصلی محترم مدنظر قرار گرفته و موارد درخواستی در قالب مدرک دیتاشیت موتور ارائه می گردد.
6- با توجه به اینکه وندور فقط تأمین موتورهای هوایی را بر عهده دارد، لذا در VPIS فقط به داده برگه موتورها اشاره شده است. مطابق با TCL ضمیمه قرارداد با سازنده، تهیه LCS توسط هیرگان انجام میگردد.
7- با توجه به وجود صرفا موتور برقی در پکیج کولرهای هوایی (در تعهد قراردادی آبان ایرکولر)، جانمایی موردنظر در مدرک به مدرک “General Arrangement Drawings (BK-GCS-AA-120-ME-DW-0001)” ارائه میگردد.
8-گزارش های موتور بعد از ساخت ارائه می گردد لذا موارد در قالب مراحل ITP و گزارشات بازرسی به تایید بازرس و ذینفعان پروژه خواهد رسید. ضمن اینکه در انتها نیز در فاینال بوک ارائه می گردند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Maleki | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 13/Dec/2023 |  |  |  |  | Date: