## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PR-DS-0001-V01 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: Process Data Sheet for AE-2101 (A/B/C) |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0008 |  |  | Transmital Date: 2024/08/10
[5 empty] | CRS No: NISOC-CRS-BK-GCS-AA-120-PR-DS-0001_V01 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Process comments :
|  |  | 03/2294/134387 | 1403/04/10 | 1- فشار طراحی (DESIGN) آیتم AE-2101-A-B-C در مدرک BK-GCS-AA-120-PR-DS-0001-V02 به 24.5 بارگیج تغییر یافت
2- FLUID NAME با توجه به دیتاشیت کارفرما در نظر گرفته شده است. خواهشمند است در این خصوص شفاف سازی نمایید
3-فایل نیتیو HTRI برای مدرک پراسس دیتا شیت و محاسبات ترمال ارسال خواهد شد
4- مورد تایید است
5-پراسس دیتا شیت رویژن 2 با توجه به طراحی جدید کاملا ریواز شده است و ارسال می گردد .طراحی با توجه به کامنت ها تغییر یافت. در این مدرک دیتا شیت اصلی (summer case) به صورت فایل و هر دو آیتم تابستانه و زمستانه به صورت native HTRI قرار گرفت تمامی موارد تابستانه و زمستانه در مدرک محاسبات حرارتی به صورت فایل (Thermal calculation book) آمده است
کامنت های بخش مکانیک بایستی با توجه به مدرک مربوطه پاسخ داده شود و در این مدرک موارد نیاز به شفاف سازی پراسسی در نظر گرفته شده است مثلا فشار هیدروتست بر اساس آخرین کامنت PEDCOتغییر یافت
خواهشمند است در خصوص مورد برقی شفاف سازی فرمایید که در کدام مدرک کامنت پاسخ داده نشده است مطابق TCL ( ایتم 33) و موتوردیتاشیت IP55 جهت موتور دیده شده است . سرویس فاکتور 1.8 نیز مربوط به بلت و پولی می باشد موتور با توجه به API 661-clause 7.2.7.1.2 سایز شده است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Maleki | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 13/Dec/2023 |  |  |  |  | Date: