## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-AA-120-IN-DS-0003_V00 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: I/P CONVERTER DATA SHEET |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0024 |  |  | Transmital Date: 2024/10/02
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-AA-120-IN-DS-0003_V00 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | power supply مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما اعمال گردید .
2 | فشار Input Air Supply مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما همانطور که در کاتالوگ اشاره شده است ، این مقدار 0.13 ~ 0.16 MPa (1.3 ~ 1.6 bar) می باشد.
3 | دقت مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما اعمال گردید .
4 | مشخص گردد که تجهیز مورد نظر Linear می باشد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما اعمال گردید .
5 | Zero and span adjustment در نظر گرفته شود. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما در نظر گرفته شده است .
6 | Fail Safe Feature مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | این مورد جهت I/P Converter ، کارایی ندارد . خواهشمند است شفاف سازی بفرمایید .
7 | Response Time مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | این مورد جهت I/P Converter ، کارایی ندارد . خواهشمند است شفاف سازی بفرمایید .
7 | Mounting مشخص گردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-09-08 | احتراما اعمال گردید .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.AKBARI | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 8 sep 2024 |  |  |  |  | Date: