## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PR-DS-0002-V02 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date: |  | HIRGAN Clarifications
Document Title: Process Data Sheet for AE-2102 (A/B/C) |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0019 |  |  | Transmital Date: 2024/10/06
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-PR-DS-0002_V02 |  |  | CRS Status: | CM
| Comments (PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سایز صحیح نازلهای ورودی و خروجی Air Cooler ها بر اساس P&ID پروژه 6 اینچ می باشد. |  | BK-SUR-ENG-MEC-03-09476 | 24/Aug/2024 | میزان RV2 که عامل تایین کننده این در سایز نازل است در 6" زیر Kg/m-s2 1000 میرود که مناسب سیال گازی نیست |  |  |  |  | با ارائه توضیحات مربوطه (مبنی بر worst case بودن طراحی با مینیمم رطوت هوا ) بدون تغییر بماند.
2 | تاثیر ماکزیمم میزان رطوبت هوا در طراحی مدنظر قرار گیرد. |  | BK-SUR-ENG-MEC-03-09476 | 24/Aug/2024 | [5 empty] | با ارائه توضیحات مربوطه (مبنی بر گیج بودن فشارها و اینکه static pressure مندرج در report از نتایج شبیه سازی است) بدون تغییر بماند.
3 | Static Pressure مطابق اطلاعات Site Condition تصحیح گردد. |  | BK-SUR-ENG-MEC-03-09476 | 24/Aug/2024 | فشار استاتیکی بر اساس طراحی کولر و استاندارد مد نظر در نظر گرفته خواهد شد لذا خواهشمند است در این خصوص شفاف سازی نمایید |  |  |  |  | با ارائه توضیحات مربوطه (مبنی بر گیج بودن فشارها و اینکه static pressure مندرج در report از نتایج شبیه سازی است) بدون تغییر بماند.
4 | فشار ورودی به مقدار کمی با فشار اعلامی PFD شرکت هوایار تفاوت دارد. |  | BK-SUR-ENG-MEC-03-09476 | 24/Aug/2024 | مورد تایید است و بر اساس مدرک BK-GCS-HY-120-PR-PF-0001-V04-AP تغییر یافت
5 | ساير نقطه نظرات در قايل پيوست قيد شده است. |  | BK-SUR-ENG-MEC-03-09476 | 24/Aug/2024 | 1-Instruments connection shall be in compliance with project instrument SPC(sizes,types,rating,....) 2-hirgan shall consider instrument items in P&ID and instrument list. AAC Reply: Based on instrument document D03 only TI connection size (1/2")is considered and all other connections are for piping not equipment, so please clarify PI connection size 3-gas group shall be considered IIC". AAC Reply: Based on TCL, DOC.NO:GCS - TCL with ABAN AIRCOOLER- Rev 03, IIB is considered if IIC is required please be noted that it will be considered with cost impact 4-pls recheck Blade no.s AAC Reply: Noted and it will be finalized after sub vendor finalization, fan data sheet rev03 will be attached too
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.MALEKI | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 19/08/2024 |  |  |  |  | Date: