## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-AA-120-IN-DS-0003_V01 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: I/P CONVERTER DATA SHEET |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0028 |  |  | Transmital Date: 2024/11/11
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-AA-120-IN-DS-0003_V01 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | منظور از Fail safe بودن به این معناست که اگر سیگنال ورودی Fail کند یا invalid باشد، خروجی فشار در زمان مشخصی به یک مقدار ثابت برگردد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-11-05 | احتراما جهت این اقلام fail safe بودن بایستی جهت بلیدهای فن تعریف گردد .که در وقوع این حالت ( fail خط هوا به بلیدها به ماکزیمم blade angle بروند و یا minium blade angle )
2 | منظور از Response time، زمان تغییرات فشار نسبت به سیگنال ورودی می باشد. |  | BK-SUR-ENG-MEC-03-09518 | 2024-11-05 | احتراما اعمال گردید .
V01
1 | با توجه به تایید کارفرما،‌ در این مقطع نقطه نظر خاصی مطرح نمی باشد. |  |  | 2024-10-19 | مورد تایید است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.AKBARI | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 19 Oct 2024 |  |  |  |  | Date: