| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Steel Structure Calculation Books نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| V01 | JAN. 2025 | IFA | AAC | M.FAKHARIAN | S.FRAMARZPOUR |  |
| V00 | MAR. 2024 | IFA | AAC | M.FAKHARIAN | S.FRAMARZPOUR |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Status: | IFA: Issued For Approval IFI: Issued For Information AFC: Approved For Construction |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | V00 | V01 | V02 | V03 | V04 |  | PAGE | V00 | V01 | V02 | V03 | V04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X |  |  |  |  | 64 |  |  |  |  |  |
| 2 | X | X |  |  |  |  | 65 |  |  |  |  |  |
| 3 | X | X |  |  |  |  | 66 |  |  |  |  |  |
| 4 | X | X |  |  |  |  | 67 |  |  |  |  |  |
| 5 | X | X |  |  |  |  | 68 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 7 | X | X |  |  |  |  | 70 |  |  |  |  |  |
| 8 | X | X |  |  |  |  | 71 |  |  |  |  |  |
| 9 | X | X |  |  |  |  | 72 |  |  |  |  |  |
| 10 | X | X |  |  |  |  | 73 |  |  |  |  |  |
| 11 | X | X |  |  |  |  | 74 |  |  |  |  |  |
| 12 | X | X |  |  |  |  | 75 |  |  |  |  |  |
| 13 | X | X |  |  |  |  | 76 |  |  |  |  |  |
| 14 | X | X |  |  |  |  | 77 |  |  |  |  |  |
| 15 | X | X |  |  |  |  | 78 |  |  |  |  |  |
| 16 | X | X |  |  |  |  | 79 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 18 | X | X |  |  |  |  | 81 |  |  |  |  |  |
| 19 | X | X |  |  |  |  | 82 |  |  |  |  |  |
| 20 | X | X |  |  |  |  | 83 |  |  |  |  |  |
| 21 | X | X |  |  |  |  | 84 |  |  |  |  |  |
| 22 | X | X |  |  |  |  | 85 |  |  |  |  |  |
| 23 | X | X |  |  |  |  | 86 |  |  |  |  |  |
| 24 | X | X |  |  |  |  | 87 |  |  |  |  |  |
| 25 | X | X |  |  |  |  | 88 |  |  |  |  |  |
| 26 | X | X |  |  |  |  | 89 |  |  |  |  |  |
| 27 | X | X |  |  |  |  | 90 |  |  |  |  |  |
| 28 | X | X |  |  |  |  | 91 |  |  |  |  |  |
| 29 | X | X |  |  |  |  | 92 |  |  |  |  |  |
| 30 | X | X |  |  |  |  | 93 |  |  |  |  |  |
| 31 | X | X |  |  |  |  | 94 |  |  |  |  |  |
| 32 | X | X |  |  |  |  | 95 |  |  |  |  |  |
| 33 |  | X |  |  |  |  | 96 |  |  |  |  |  |
| 34 |  | X |  |  |  |  | 97 |  |  |  |  |  |
| 35 |  | X |  |  |  |  | 98 |  |  |  |  |  |
| 36 |  | X |  |  |  |  | 99 |  |  |  |  |  |
| 37 |  | X |  |  |  |  | 100 |  |  |  |  |  |
| 38 |  | X |  |  |  |  | 101 |  |  |  |  |  |
| 39 |  | X |  |  |  |  | 102 |  |  |  |  |  |
| 40 |  | X |  |  |  |  | 103 |  |  |  |  |  |
| 41 |  | X |  |  |  |  | 104 |  |  |  |  |  |
| 42 |  | X |  |  |  |  | 105 |  |  |  |  |  |
| 43 |  | X |  |  |  |  | 106 |  |  |  |  |  |
| 44 |  | X |  |  |  |  | 107 |  |  |  |  |  |
| 45 |  | X |  |  |  |  | 108 |  |  |  |  |  |
| 46 |  | X |  |  |  |  | 109 |  |  |  |  |  |
| 47 |  | X |  |  |  |  | 110 |  |  |  |  |  |
| 48 |  | X |  |  |  |  | 111 |  |  |  |  |  |
| 49 |  | X |  |  |  |  | 112 |  |  |  |  |  |
| 50 |  | X |  |  |  |  | 113 |  |  |  |  |  |
| 51 |  | X |  |  |  |  | 114 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 126 |  |  |  |  |  |

Contents

1	INTRODUCTION	4

2	Scope	4

3	Codes & Standards	4

4	Reference Drawing & General Document:	4

5	Materials	4

6	Descriptions of Supported Equipment:	5

7	EXTERNAL LOADS	6

8	ANALYISIS	30

9	DESIGN	32

10	DESIGN OUTPUT	45

11	DISPLACEMENT CONTROL	49

- INTRODUCTION:

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

- SCOPE:

This calculation book covers a structural design for air cooler AE2101/AE2102.

3-dimensional model analysed by means of SAP-2000 software VER. 24.2.0.

This report contains computerized model, load evaluation and design verification.

- CODES AND STANDARDS:

# American Institute of Steel Construction.  (AISC 360-16)

Minimum Design Loads and Associated Criteria for Buildings and Other Structures (ASCE-7-16)

1

Iranian National Regulations of Buldings (INBC part 10, INBC6)

- REFERENCE DRAWING & GENERAL DOCUMENT:

# General Arrangement Drawings: (BK-GCS-AA-120-ME-DW-0001)

- MATERIALS:

- Structural Steel: S235JR (ST-37)

With   Fy = 2400 kg/cm²   & Fu = 3700 kg/cm²

- Bolts: A325 (ASTM.) or equivalent HR 8.8 (DIN.)

With   Fu = 8000 kg/cm²

- Anchor Bolts: ISIR/ISO 4.6 or equivalent A307 With   Fu = 4000 kg/cm²

1

DESCRIPTIONS OF SUPPORTED EQUIPMENT:

- Draft: Induced

- Weight:

| WEIGTH (kg)-ITEM: 2101 |  |  |  |
| --- | --- | --- | --- |
| BUNDLE + SIDE FRAME + LOUVER (DRY PER BAY): | 2344 | FAN + FAN GUARD (PER BAY): | 400 |
| BUNDLE + SIDE FRAME + LOUVER (OPERATION PER BAY): | 2349 | MOTOR + MOTOR SUPPORT (PER BAY): | 1000 |
| BUNDLE + SIDE FRAME + LOUVER (HYDRO TEST PER BAY): | 2624 | REDUCTION SYSTEM (PER BAY): | 600 |
| PLENUME + FAN RING (PER BAY): | 900 | STATIC PRESSURE DROP (Pa): | 152.81 |

| WEIGTH (kg) - 2102 |  |  |  |
| --- | --- | --- | --- |
| BUNDLE + SIDE FRAME + LOUVER (DRY PER BAY): | 3212 | FAN + FAN GUARD (PER BAY): | 400 |
| BUNDLE + SIDE FRAME + LOUVER (OPERATION PER BAY): | 3649 | MOTOR + MOTOR SUPPORT (PER BAY): | 1000 |
| BUNDLE + SIDE FRAME + LOUVER (HYDRO TEST PER BAY): | 3657 | REDUCTION SYSTEM (PER BAY): | 600 |
| PLENUME + FAN RING (PER BAY): | 900 | STATIC PRESSURE DROP (Pa): | 173.10 |

# EXTERNAL LOADS

# Load Case Definition:

# -  Dead Load (DLs): Contain weight of steel structure & 20 percent weight of steel structure

# as structural connection and dead load of walk way.

# -  Empty Dead Load (DL): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan

# guard, motor, motor support, reduction system).

# -   Live Load (L): Live load of walkway and load due to static pressure drop of fan.

# -   Operation Load (EO): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan

# guard, motor, motor support, reduction system) and fluid weight that flows in bundles in

# operation.

# -  Test Load (ET): The dead load of equipment (bundle dry, plenum, fan ring, fan, fan guard,

# motor, motor support, reduction system) and Water weight that flows in bundles in hydro

# test.

# -  ELX:  Effect of earth quake at x- direction.

# -  ELY:  Effect of earth quake at y- direction.

# -  WLX:  Effect of wind load at x- direction.

# -  WLY:  Effect of wind load at y- direction.

# -  Snow Load (SL): Snow load shall be taken as 150 kg/m2 as per site information and shall be

# uniformly distributed over the horizontal projection of the loaded areas.

# -  TL: Thermal load.

1

1

1

| Header Walkway Loads: |  |  |  |
| --- | --- | --- | --- |
| Weight of Grating = |  | 45 | kg/m² |
| Rail = |  | 55 | kg/m2 |
|  | Width of Walkway = | 0.8 | m |
|  | Dead Load for Walkway Beams: | 40 | kg/m |
|  | Live Load for Walkway = | 500 | kg/m² |
|  | Live Load for Walkway Beams: | 200 | kg/m |
|  | Snow Load for Walkway = | 50 | kg/m² |
|  | Snow Load for Walkway Beams= | 26 | kg/m |

| Motor Walkway Loads: |  |  |  |
| --- | --- | --- | --- |
| Weight of Grating = |  | 45 | kg/m² |
| Rail = |  | 55 | kg/m2 |
|  | Width of Walkway = | 1.2 | m |
|  | Dead Load for Walkway Beams= | 60 | kg/m |
|  | Live Load for Walkway = | 500 | kg/m² |
|  | Live Load for Walkway Beams= | 300 | kg/m |

1

EARTHQUAKE   LOADS:

1

WIND LOADS:

17208-2101:

1

17208-2102:

1

WLXP:

1

WLXN:

1

WLYP:

1

WLYN:

1

WLXP:

WLXN:

WLYP:

WLYN:

- Ambient Temperature ± 35°C

1

- DL (Dead load):

1

LL (Dead load):

1

EO (Opration load):

1

ET (Test load):

1

SL (Snow load):

1

HYD :

1

OCC+Y :

1

OCC-Y :

1

OPE-1 :

1

OPE-2 :

1

SUS :

1

FIRE PROOFING FOR COLUMN & MAIN BRACES :

1

FIRE PROOFING FOR BEAMS :

1

ANALYSIS:

3D Computerized Model:

Analysis input data:

| Mass Source According ASCE7: TABLE: Masses 1 - Mass Source. Mass From; Load Pat; Multiplier. Text; Text; Unitless. Loads; DLS; 1. Loads; DL; 1. Loads; EO; 1. Loads; LL; 0.25. Loads; SL; 0.2. | : |
| --- | --- |
| 1 Load Pattern Definitions: TABLE: Load Pattern Definitions. LoadPat; DesignType; SelfWtMult; AutoLoad; NotBasePat; NotRatio; NotDir. Text; Text; Unitless; Text; Text; Unitless; Text. DLS; Dead; 1.2. DL; Dead; 0. EO; Dead; 0. ET; Dead; 0. LL; Live; 0. SL; Snow; 0. WLXP; Wind; 0; ASCE 7-16. WLXN; Wind; 0; ASCE 7-16. WLYP; Wind; 0; ASCE 7-16. WLYN; Wind; 0; ASCE 7-16. ELX; Quake; 0; USER COEFF. ELY; Quake; 0; USER COEFF. TL; Temperature; 0. NXDLS; Notional; 0; DLS; 0.002; Global X. NYDLS; Notional; 0; DLS; 0.002; Global Y. NXDL; Notional; 0; DL; 0.002; Global X. NYDL; Notional; 0; DL; 0.002; Global Y. NXEO; Notional; 0; EO; 0.002; Global X. NYEO; Notional; 0; EO; 0.002; Global Y. NXLL; Notional; 0; LL; 0.002; Global X. NYLL; Notional; 0; LL; 0.002; Global Y. HYD; Other; 0. OPE-1; Other; 0. OPE-2; Other; 0. SUS; Other; 0. OCC+Y; Other; 0. OCC-Y; Other; 0. |  |

1

Auto Seismic - User Coefficient:

| TABLE: Auto Seismic - User Coefficient |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LoadPat | Dir | PercentEcc | EccOverride | UserZ | C | K | WeightUsed | BaseShear |
| Text | Text | Unitless | Yes/No | Yes/No | Unitless | Unitless | Kgf | Kgf |
| ELX | X | 0.05 | No | No | 0.319 | 1 | 27569.07 | 7939.89 |
| ELY | Y | 0.05 | No | No | 0.319 | 1 | 27569.27 | 7939.89 |

1

DESIGN:

General Load Combination: (INBC6)

| TABLE: Combination Definitions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ComboName | ComboType | AutoDesign | CaseType | CaseName | ScaleFactor | SteelDesign |
| Text | Text | Yes/No | Text | Text | Unitless | Text |
| EM1 | Linear Add | No | Linear Static | DL | 1.4 | Strength |
| EM1 |  |  | Linear Static | DLs | 1.4 |  |
| EM2 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM2 |  |  | Linear Static | DLs | 1.2 |  |
| EM3 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM3 |  |  | Linear Static | DLs | 1.2 |  |
| EM3 |  |  | Linear Static | WLXP | 1.6 |  |
| EM4 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM4 |  |  | Linear Static | DLs | 1.2 |  |
| EM4 |  |  | Linear Static | WLXN | 1.6 |  |
| EM5 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM5 |  |  | Linear Static | DLs | 1.2 |  |
| EM5 |  |  | Linear Static | WLYP | 1.6 |  |
| EM6 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM6 |  |  | Linear Static | DLs | 1.2 |  |
| EM6 |  |  | Linear Static | WLYN | 1.6 |  |
| EM7 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM7 |  |  | Linear Static | DLs | 1.35 |  |
| EM7 |  |  | Linear Static | ELX | 1 |  |
| EM7 |  |  | Linear Static | ELY | 0.3 |  |
| EM8 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM8 |  |  | Linear Static | DLs | 1.35 |  |
| EM8 |  |  | Linear Static | ELX | 1 |  |
| EM8 |  |  | Linear Static | ELY | -0.3 |  |
| EM9 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM9 |  |  | Linear Static | DLs | 1.35 |  |
| EM9 |  |  | Linear Static | ELX | -1 |  |
| EM9 |  |  | Linear Static | ELY | 0.3 |  |
| EM10 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM10 |  |  | Linear Static | DLs | 1.35 |  |
| EM10 |  |  | Linear Static | ELX | -1 |  |
| EM10 |  |  | Linear Static | ELY | -0.3 |  |
| EM11 | Linear Add | No | Linear Static | DL | 1.36 | Strength |
| EM11 |  |  | Linear Static | DLs | 1.35 |  |
| EM11 |  |  | Linear Static | ELY | 1 |  |
| EM11 |  |  | Linear Static | ELX | 0.3 |  |
| EM12 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM12 |  |  | Linear Static | DLs | 1.35 |  |
| EM12 |  |  | Linear Static | ELY | 1 |  |
| EM12 |  |  | Linear Static | ELX | -0.3 |  |
| EM13 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM13 |  |  | Linear Static | DLs | 1.35 |  |
| EM13 |  |  | Linear Static | ELY | -1 |  |
| EM13 |  |  | Linear Static | ELX | 0.3 |  |
| EM14 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| EM14 |  |  | Linear Static | DLs | 1.35 |  |
| EM14 |  |  | Linear Static | ELY | -1 |  |
| EM14 |  |  | Linear Static | ELX | -0.3 |  |
| EM15 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| EM15 |  |  | Linear Static | DLs | 0.9 |  |
| EM15 |  |  | Linear Static | WLXP | 1.6 |  |
| EM16 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| EM16 |  |  | Linear Static | DLs | 0.9 |  |
| EM16 |  |  | Linear Static | WLXN | 1.6 |  |
| EM17 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| EM17 |  |  | Linear Static | DLs | 0.9 |  |
| EM17 |  |  | Linear Static | WLYP | 1.6 |  |
| EM18 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| EM18 |  |  | Linear Static | DLs | 0.9 |  |
| EM18 |  |  | Linear Static | WLYN | 1.6 |  |
| EM19 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM19 |  |  | Linear Static | DLs | 0.75 |  |
| EM19 |  |  | Linear Static | ELX | 1 |  |
| EM19 |  |  | Linear Static | ELY | 0.3 |  |
| EM20 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM20 |  |  | Linear Static | DLs | 0.75 |  |
| EM20 |  |  | Linear Static | ELX | 1 |  |
| EM20 |  |  | Linear Static | ELY | -0.3 |  |
| EM21 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM21 |  |  | Linear Static | DLs | 0.75 |  |
| EM21 |  |  | Linear Static | ELX | -1 |  |
| EM21 |  |  | Linear Static | ELY | 0.3 |  |
| EM22 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM22 |  |  | Linear Static | DLs | 0.75 |  |
| EM22 |  |  | Linear Static | ELX | -1 |  |
| EM22 |  |  | Linear Static | ELY | -0.3 |  |
| EM23 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM23 |  |  | Linear Static | DLs | 0.75 |  |
| EM23 |  |  | Linear Static | ELY | 1 |  |
| EM23 |  |  | Linear Static | ELX | 0.3 |  |
| EM24 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM24 |  |  | Linear Static | DLs | 0.75 |  |
| EM24 |  |  | Linear Static | ELY | 1 |  |
| EM24 |  |  | Linear Static | ELX | -0.3 |  |
| EM25 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM25 |  |  | Linear Static | DLs | 0.75 |  |
| EM25 |  |  | Linear Static | ELY | -1 |  |
| EM25 |  |  | Linear Static | ELX | 0.3 |  |
| EM26 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| EM26 |  |  | Linear Static | DLs | 0.75 |  |
| EM26 |  |  | Linear Static | ELY | -1 |  |
| EM26 |  |  | Linear Static | ELX | -0.3 |  |
| EM27 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM27 |  |  | Linear Static | DLs | 1.2 |  |
| EM28 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM28 |  |  | Linear Static | DLs | 1.2 |  |
| EM28 |  |  | Linear Static | WLXN | 0.8 |  |
| EM29 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM29 |  |  | Linear Static | DLs | 1.2 |  |
| EM29 |  |  | Linear Static | WLXP | 0.8 |  |
| EM30 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM30 |  |  | Linear Static | DLs | 1.2 |  |
| EM30 |  |  | Linear Static | WLYP | 0.8 |  |
| EM31 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| EM31 |  |  | Linear Static | DLs | 1.2 |  |
| EM31 |  |  | Linear Static | WLYN | 0.8 |  |
| TE1 | Linear Add | No | Linear Static | DL | 1.4 | Strength |
| TE1 |  |  | Linear Static | DLs | 1.4 |  |
| TE1 |  |  | Linear Static | ET | 1.4 |  |
| TE2 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE2 |  |  | Linear Static | DLs | 1.2 |  |
| TE2 |  |  | Linear Static | ET | 1.2 |  |
| TE2 |  |  | Linear Static | LL | 1.6 |  |
| TE2 |  |  | Linear Static | SL | 0.5 |  |
| TE3 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE3 |  |  | Linear Static | DLs | 1.2 |  |
| TE3 |  |  | Linear Static | WLXP | 1.6 |  |
| TE3 |  |  | Linear Static | ET | 1.2 |  |
| TE3 |  |  | Linear Static | LL | 1 |  |
| TE3 |  |  | Linear Static | SL | 0.5 |  |
| TE4 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE4 |  |  | Linear Static | DLs | 1.2 |  |
| TE4 |  |  | Linear Static | WLXN | 1.6 |  |
| TE4 |  |  | Linear Static | ET | 1.2 |  |
| TE4 |  |  | Linear Static | LL | 1 |  |
| TE4 |  |  | Linear Static | SL | 0.5 |  |
| TE5 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE5 |  |  | Linear Static | DLs | 1.2 |  |
| TE5 |  |  | Linear Static | WLYP | 1.6 |  |
| TE5 |  |  | Linear Static | ET | 1.2 |  |
| TE5 |  |  | Linear Static | LL | 1 |  |
| TE5 |  |  | Linear Static | SL | 0.5 |  |
| TE6 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE6 |  |  | Linear Static | DLs | 1.2 |  |
| TE6 |  |  | Linear Static | WLYN | 1.6 |  |
| TE6 |  |  | Linear Static | ET | 1.2 |  |
| TE6 |  |  | Linear Static | LL | 1 |  |
| TE6 |  |  | Linear Static | SL | 0.5 |  |
| TE7 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE7 |  |  | Linear Static | DLs | 1.35 |  |
| TE7 |  |  | Linear Static | ET | 1.35 |  |
| TE7 |  |  | Linear Static | ELX | 1 |  |
| TE7 |  |  | Linear Static | ELY | 0.3 |  |
| TE7 |  |  | Linear Static | LL | 1.35 |  |
| TE7 |  |  | Linear Static | SL | 0.2 |  |
| TE8 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE8 |  |  | Linear Static | DLs | 1.35 |  |
| TE8 |  |  | Linear Static | ET | 1.35 |  |
| TE8 |  |  | Linear Static | ELX | 1 |  |
| TE8 |  |  | Linear Static | ELY | -0.3 |  |
| TE8 |  |  | Linear Static | LL | 1.35 |  |
| TE8 |  |  | Linear Static | SL | 0.2 |  |
| TE9 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE9 |  |  | Linear Static | DLs | 1.35 |  |
| TE9 |  |  | Linear Static | ET | 1.35 |  |
| TE9 |  |  | Linear Static | ELX | -1 |  |
| TE9 |  |  | Linear Static | ELY | 0.3 |  |
| TE9 |  |  | Linear Static | LL | 1.35 |  |
| TE9 |  |  | Linear Static | SL | 0.2 |  |
| TE10 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE10 |  |  | Linear Static | DLs | 1.35 |  |
| TE10 |  |  | Linear Static | ET | 1.35 |  |
| TE10 |  |  | Linear Static | ELX | -1 |  |
| TE10 |  |  | Linear Static | ELY | -0.3 |  |
| TE10 |  |  | Linear Static | LL | 1.35 |  |
| TE10 |  |  | Linear Static | SL | 0.2 |  |
| TE11 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE11 |  |  | Linear Static | DLs | 1.35 |  |
| TE11 |  |  | Linear Static | ET | 1.35 |  |
| TE11 |  |  | Linear Static | ELY | 1 |  |
| TE11 |  |  | Linear Static | ELX | 0.3 |  |
| TE11 |  |  | Linear Static | LL | 1.35 |  |
| TE11 |  |  | Linear Static | SL | 0.2 |  |
| TE12 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE12 |  |  | Linear Static | DLs | 1.35 |  |
| TE12 |  |  | Linear Static | ET | 1.35 |  |
| TE12 |  |  | Linear Static | ELY | 1 |  |
| TE12 |  |  | Linear Static | ELX | -0.3 |  |
| TE12 |  |  | Linear Static | LL | 1.35 |  |
| TE12 |  |  | Linear Static | SL | 0.2 |  |
| TE13 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE13 |  |  | Linear Static | DLs | 1.35 |  |
| TE13 |  |  | Linear Static | ET | 1.35 |  |
| TE13 |  |  | Linear Static | ELY | -1 |  |
| TE13 |  |  | Linear Static | ELX | 0.3 |  |
| TE13 |  |  | Linear Static | LL | 1.35 |  |
| TE13 |  |  | Linear Static | SL | 0.2 |  |
| TE14 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| TE14 |  |  | Linear Static | DLs | 1.35 |  |
| TE14 |  |  | Linear Static | ET | 1.35 |  |
| TE14 |  |  | Linear Static | ELY | -1 |  |
| TE14 |  |  | Linear Static | ELX | -0.3 |  |
| TE14 |  |  | Linear Static | SL | 0.2 |  |
| TE14 |  |  | Linear Static | LL | 1.35 |  |
| TE15 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| TE15 |  |  | Linear Static | DLs | 0.9 |  |
| TE15 |  |  | Linear Static | WLXP | 1.6 |  |
| TE15 |  |  | Linear Static | ET | 0.9 |  |
| TE16 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| TE16 |  |  | Linear Static | DLs | 0.9 |  |
| TE16 |  |  | Linear Static | WLXN | 1.6 |  |
| TE16 |  |  | Linear Static | ET | 0.9 |  |
| TE17 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| TE17 |  |  | Linear Static | DLs | 0.9 |  |
| TE17 |  |  | Linear Static | WLYP | 1.6 |  |
| TE17 |  |  | Linear Static | ET | 0.9 |  |
| TE18 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| TE18 |  |  | Linear Static | DLs | 0.9 |  |
| TE18 |  |  | Linear Static | WLYN | 1.6 |  |
| TE18 |  |  | Linear Static | ET | 0.9 |  |
| TE19 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE19 |  |  | Linear Static | DLs | 0.75 |  |
| TE19 |  |  | Linear Static | ET | 0.75 |  |
| TE19 |  |  | Linear Static | ELX | 1 |  |
| TE19 |  |  | Linear Static | ELY | 0.3 |  |
| TE20 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE20 |  |  | Linear Static | DLs | 0.75 |  |
| TE20 |  |  | Linear Static | ET | 0.75 |  |
| TE20 |  |  | Linear Static | ELX | 1 |  |
| TE20 |  |  | Linear Static | ELY | -0.3 |  |
| TE21 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE21 |  |  | Linear Static | DLs | 0.75 |  |
| TE21 |  |  | Linear Static | ET | 0.75 |  |
| TE21 |  |  | Linear Static | ELX | -1 |  |
| TE21 |  |  | Linear Static | ELY | 0.3 |  |
| TE22 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE22 |  |  | Linear Static | DLs | 0.75 |  |
| TE22 |  |  | Linear Static | ET | 0.75 |  |
| TE22 |  |  | Linear Static | ELX | -1 |  |
| TE22 |  |  | Linear Static | ELY | -0.3 |  |
| TE23 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE23 |  |  | Linear Static | DLs | 0.75 |  |
| TE23 |  |  | Linear Static | ET | 0.75 |  |
| TE23 |  |  | Linear Static | ELY | 1 |  |
| TE23 |  |  | Linear Static | ELX | 0.3 |  |
| TE24 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE24 |  |  | Linear Static | DLs | 0.75 |  |
| TE24 |  |  | Linear Static | ET | 0.75 |  |
| TE24 |  |  | Linear Static | ELY | 1 |  |
| TE24 |  |  | Linear Static | ELX | -0.3 |  |
| TE25 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE25 |  |  | Linear Static | DLs | 0.75 |  |
| TE25 |  |  | Linear Static | ET | 0.75 |  |
| TE25 |  |  | Linear Static | ELY | -1 |  |
| TE25 |  |  | Linear Static | ELX | 0.3 |  |
| TE26 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| TE26 |  |  | Linear Static | DLs | 0.75 |  |
| TE26 |  |  | Linear Static | ET | 0.75 |  |
| TE26 |  |  | Linear Static | ELY | -1 |  |
| TE26 |  |  | Linear Static | ELX | -0.3 |  |
| TE27 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE27 |  |  | Linear Static | DLs | 1.2 |  |
| TE27 |  |  | Linear Static | ET | 1.2 |  |
| TE27 |  |  | Linear Static | SL | 1.6 |  |
| TE27 |  |  | Linear Static | LL | 1 |  |
| TE28 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE28 |  |  | Linear Static | DLs | 1.2 |  |
| TE28 |  |  | Linear Static | ET | 1.2 |  |
| TE28 |  |  | Linear Static | WLXN | 0.8 |  |
| TE28 |  |  | Linear Static | SL | 1.6 |  |
| TE29 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE29 |  |  | Linear Static | DLs | 1.2 |  |
| TE29 |  |  | Linear Static | ET | 1.2 |  |
| TE29 |  |  | Linear Static | WLXP | 0.8 |  |
| TE29 |  |  | Linear Static | SL | 1.6 |  |
| TE30 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE30 |  |  | Linear Static | DLs | 1.2 |  |
| TE30 |  |  | Linear Static | ET | 1.2 |  |
| TE30 |  |  | Linear Static | WLYN | 0.8 |  |
| TE30 |  |  | Linear Static | SL | 1.6 |  |
| TE31 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TE31 |  |  | Linear Static | DLs | 1.2 |  |
| TE31 |  |  | Linear Static | ET | 1.2 |  |
| TE31 |  |  | Linear Static | WLYP | 0.8 |  |
| TE31 |  |  | Linear Static | SL | 1.6 |  |
| OP1 | Linear Add | No | Linear Static | DL | 1.4 | Strength |
| OP1 |  |  | Linear Static | DLs | 1.4 |  |
| OP1 |  |  | Linear Static | EO | 1.4 |  |
| OP1 |  |  | Linear Static | OP | 1.4 |  |
| OP2 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP2 |  |  | Linear Static | DLs | 1.2 |  |
| OP2 |  |  | Linear Static | EO | 1.2 |  |
| OP2 |  |  | Linear Static | LL | 1.6 |  |
| OP2 |  |  | Linear Static | SL | 0.5 |  |
| OP2 |  |  | Linear Static | OP | 1.2 |  |
| OP3 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP3 |  |  | Linear Static | DLs | 1.2 |  |
| OP3 |  |  | Linear Static | WLXP | 1.6 |  |
| OP3 |  |  | Linear Static | EO | 1.2 |  |
| OP3 |  |  | Linear Static | LL | 1 |  |
| OP3 |  |  | Linear Static | SL | 0.5 |  |
| OP3 |  |  | Linear Static | OP | 1.2 |  |
| OP4 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP4 |  |  | Linear Static | DLs | 1.2 |  |
| OP4 |  |  | Linear Static | WLXN | 1.6 |  |
| OP4 |  |  | Linear Static | EO | 1.2 |  |
| OP4 |  |  | Linear Static | LL | 1 |  |
| OP4 |  |  | Linear Static | SL | 0.5 |  |
| OP4 |  |  | Linear Static | OP | 1.2 |  |
| OP5 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP5 |  |  | Linear Static | DLs | 1.2 |  |
| OP5 |  |  | Linear Static | WLYP | 1.6 |  |
| OP5 |  |  | Linear Static | EO | 1.2 |  |
| OP5 |  |  | Linear Static | LL | 1 |  |
| OP5 |  |  | Linear Static | SL | 0.5 |  |
| OP5 |  |  | Linear Static | OP | 1.2 |  |
| OP6 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP6 |  |  | Linear Static | DLs | 1.2 |  |
| OP6 |  |  | Linear Static | WLYN | 1.6 |  |
| OP6 |  |  | Linear Static | EO | 1.2 |  |
| OP6 |  |  | Linear Static | LL | 1 |  |
| OP6 |  |  | Linear Static | SL | 0.5 |  |
| OP6 |  |  | Linear Static | OP | 1.2 |  |
| OP7 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP7 |  |  | Linear Static | DLs | 1.35 |  |
| OP7 |  |  | Linear Static | EO | 1.35 |  |
| OP7 |  |  | Linear Static | ELX | 1 |  |
| OP7 |  |  | Linear Static | ELY | 0.3 |  |
| OP7 |  |  | Linear Static | LL | 1.35 |  |
| OP7 |  |  | Linear Static | SL | 0.2 |  |
| OP7 |  |  | Linear Static | OP | 1.35 |  |
| OP8 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP8 |  |  | Linear Static | DLs | 1.35 |  |
| OP8 |  |  | Linear Static | EO | 1.35 |  |
| OP8 |  |  | Linear Static | ELX | 1 |  |
| OP8 |  |  | Linear Static | ELY | -0.3 |  |
| OP8 |  |  | Linear Static | LL | 1.35 |  |
| OP8 |  |  | Linear Static | SL | 0.2 |  |
| OP8 |  |  | Linear Static | OP | 1.35 |  |
| OP9 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP9 |  |  | Linear Static | DLs | 1.35 |  |
| OP9 |  |  | Linear Static | EO | 1.35 |  |
| OP9 |  |  | Linear Static | ELX | -1 |  |
| OP9 |  |  | Linear Static | ELY | 0.3 |  |
| OP9 |  |  | Linear Static | LL | 1.35 |  |
| OP9 |  |  | Linear Static | SL | 0.2 |  |
| OP9 |  |  | Linear Static | OP | 1.35 |  |
| OP10 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP10 |  |  | Linear Static | DLs | 1.35 |  |
| OP10 |  |  | Linear Static | EO | 1.35 |  |
| OP10 |  |  | Linear Static | ELX | -1 |  |
| OP10 |  |  | Linear Static | ELY | -0.3 |  |
| OP10 |  |  | Linear Static | LL | 1.35 |  |
| OP10 |  |  | Linear Static | SL | 0.2 |  |
| OP10 |  |  | Linear Static | OP | 1.35 |  |
| OP11 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP11 |  |  | Linear Static | DLs | 1.35 |  |
| OP11 |  |  | Linear Static | EO | 1.35 |  |
| OP11 |  |  | Linear Static | ELY | 1 |  |
| OP11 |  |  | Linear Static | ELX | 0.3 |  |
| OP11 |  |  | Linear Static | LL | 1.35 |  |
| OP11 |  |  | Linear Static | SL | 0.2 |  |
| OP11 |  |  | Linear Static | OP | 1.35 |  |
| OP12 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP12 |  |  | Linear Static | DLs | 1.35 |  |
| OP12 |  |  | Linear Static | EO | 1.35 |  |
| OP12 |  |  | Linear Static | ELY | 1 |  |
| OP12 |  |  | Linear Static | ELX | -0.3 |  |
| OP12 |  |  | Linear Static | LL | 1.35 |  |
| OP12 |  |  | Linear Static | SL | 0.2 |  |
| OP12 |  |  | Linear Static | OP | 1.35 |  |
| OP13 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP13 |  |  | Linear Static | DLs | 1.35 |  |
| OP13 |  |  | Linear Static | EO | 1.35 |  |
| OP13 |  |  | Linear Static | ELY | -1 |  |
| OP13 |  |  | Linear Static | ELX | 0.3 |  |
| OP13 |  |  | Linear Static | LL | 1.35 |  |
| OP13 |  |  | Linear Static | SL | 0.2 |  |
| OP13 |  |  | Linear Static | OP | 1.35 |  |
| OP14 | Linear Add | No | Linear Static | DL | 1.35 | Strength |
| OP14 |  |  | Linear Static | DLs | 1.35 |  |
| OP14 |  |  | Linear Static | EO | 1.35 |  |
| OP14 |  |  | Linear Static | ELY | -1 |  |
| OP14 |  |  | Linear Static | ELX | -0.3 |  |
| OP14 |  |  | Linear Static | LL | 1.35 |  |
| OP14 |  |  | Linear Static | SL | 0.2 |  |
| OP14 |  |  | Linear Static | OP | 1.35 |  |
| OP15 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| OP15 |  |  | Linear Static | DLs | 0.9 |  |
| OP15 |  |  | Linear Static | WLXP | 1.6 |  |
| OP15 |  |  | Linear Static | EO | 0.9 |  |
| OP15 |  |  | Linear Static | OP | 0.9 |  |
| OP16 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| OP16 |  |  | Linear Static | DLs | 0.9 |  |
| OP16 |  |  | Linear Static | WLXN | 1.6 |  |
| OP16 |  |  | Linear Static | EO | 0.9 |  |
| OP16 |  |  | Linear Static | OP | 0.9 |  |
| OP17 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| OP17 |  |  | Linear Static | DLs | 0.9 |  |
| OP17 |  |  | Linear Static | WLYP | 1.6 |  |
| OP17 |  |  | Linear Static | EO | 0.9 |  |
| OP17 |  |  | Linear Static | OP | 0.9 |  |
| OP18 | Linear Add | No | Linear Static | DL | 0.9 | Strength |
| OP18 |  |  | Linear Static | DLs | 0.9 |  |
| OP18 |  |  | Linear Static | WLYN | 1.6 |  |
| OP18 |  |  | Linear Static | EO | 0.9 |  |
| OP18 |  |  | Linear Static | OP | 0.9 |  |
| OP19 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP19 |  |  | Linear Static | DLs | 0.75 |  |
| OP19 |  |  | Linear Static | EO | 0.75 |  |
| OP19 |  |  | Linear Static | ELX | 1 |  |
| OP19 |  |  | Linear Static | ELY | 0.3 |  |
| OP19 |  |  | Linear Static | OP | 0.75 |  |
| OP20 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP20 |  |  | Linear Static | DLs | 0.75 |  |
| OP20 |  |  | Linear Static | EO | 0.75 |  |
| OP20 |  |  | Linear Static | ELX | 1 |  |
| OP20 |  |  | Linear Static | ELY | -0.3 |  |
| OP20 |  |  | Linear Static | OP | 0.75 |  |
| OP21 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP21 |  |  | Linear Static | DLs | 0.75 |  |
| OP21 |  |  | Linear Static | EO | 0.75 |  |
| OP21 |  |  | Linear Static | ELX | -1 |  |
| OP21 |  |  | Linear Static | ELY | 0.3 |  |
| OP21 |  |  | Linear Static | OP | 0.75 |  |
| OP22 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP22 |  |  | Linear Static | DLs | 0.75 |  |
| OP22 |  |  | Linear Static | EO | 0.75 |  |
| OP22 |  |  | Linear Static | ELX | -1 |  |
| OP22 |  |  | Linear Static | ELY | -0.3 |  |
| OP22 |  |  | Linear Static | OP | 0.75 |  |
| OP23 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP23 |  |  | Linear Static | DLs | 0.75 |  |
| OP23 |  |  | Linear Static | EO | 0.75 |  |
| OP23 |  |  | Linear Static | ELY | 1 |  |
| OP23 |  |  | Linear Static | ELX | 0.3 |  |
| OP23 |  |  | Linear Static | OP | 0.75 |  |
| OP24 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP24 |  |  | Linear Static | DLs | 0.75 |  |
| OP24 |  |  | Linear Static | EO | 0.75 |  |
| OP24 |  |  | Linear Static | ELY | 1 |  |
| OP24 |  |  | Linear Static | ELX | -0.3 |  |
| OP24 |  |  | Linear Static | OP | 0.75 |  |
| OP25 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP25 |  |  | Linear Static | DLs | 0.75 |  |
| OP25 |  |  | Linear Static | EO | 0.75 |  |
| OP25 |  |  | Linear Static | ELY | -1 |  |
| OP25 |  |  | Linear Static | ELX | 0.3 |  |
| OP25 |  |  | Linear Static | OP | 0.75 |  |
| OP26 | Linear Add | No | Linear Static | DL | 0.75 | Strength |
| OP26 |  |  | Linear Static | DLs | 0.75 |  |
| OP26 |  |  | Linear Static | EO | 0.75 |  |
| OP26 |  |  | Linear Static | ELY | -1 |  |
| OP26 |  |  | Linear Static | ELX | -0.3 |  |
| OP26 |  |  | Linear Static | OP | 0.75 |  |
| OP27 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP27 |  |  | Linear Static | DLs | 1.2 |  |
| OP27 |  |  | Linear Static | EO | 1.2 |  |
| OP27 |  |  | Linear Static | SL | 1.6 |  |
| OP27 |  |  | Linear Static | LL | 1 |  |
| OP27 |  |  | Linear Static | OP | 1.2 |  |
| OP28 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP28 |  |  | Linear Static | DLs | 1.2 |  |
| OP28 |  |  | Linear Static | EO | 1.2 |  |
| OP28 |  |  | Linear Static | WLXP | 0.8 |  |
| OP28 |  |  | Linear Static | SL | 1.6 |  |
| OP28 |  |  | Linear Static | OP | 1.2 |  |
| OP29 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP29 |  |  | Linear Static | DLs | 1.2 |  |
| OP29 |  |  | Linear Static | EO | 1.2 |  |
| OP29 |  |  | Linear Static | WLXN | 0.8 |  |
| OP29 |  |  | Linear Static | SL | 1.6 |  |
| OP29 |  |  | Linear Static | OP | 1.2 |  |
| OP30 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP30 |  |  | Linear Static | DLs | 1.2 |  |
| OP30 |  |  | Linear Static | EO | 1.2 |  |
| OP30 |  |  | Linear Static | WLYP | 0.8 |  |
| OP30 |  |  | Linear Static | SL | 1.6 |  |
| OP30 |  |  | Linear Static | OP | 1.2 |  |
| OP31 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| OP31 |  |  | Linear Static | DLs | 1.2 |  |
| OP31 |  |  | Linear Static | EO | 1.2 |  |
| OP31 |  |  | Linear Static | WLYN | 0.8 |  |
| OP31 |  |  | Linear Static | SL | 1.6 |  |
| OP31 |  |  | Linear Static | OP | 1.2 |  |
| TERMAL1 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TERMAL1 |  |  | Linear Static | DLs | 1.2 |  |
| TERMAL1 |  |  | Linear Static | TL | 1.2 |  |
| TERMAL2 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TERMAL2 |  |  | Linear Static | DLs | 1.2 |  |
| TERMAL2 |  |  | Linear Static | TL | -1.2 |  |
| TERMAL3 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TERMAL3 |  |  | Linear Static | DLs | 1.2 |  |
| TERMAL3 |  |  | Linear Static | TL | 1 |  |
| TERMAL4 | Linear Add | No | Linear Static | DL | 1.2 | Strength |
| TERMAL4 |  |  | Linear Static | DLs | 1.2 |  |
| TERMAL4 |  |  | Linear Static | TL | -1 |  |

- DESIGN OUTPUT: Steel structure checking in general combinations Axis “A”:

Axis “B”: Axis “C”:

Axis “1”: Axis “2”:

PLAN AT EL.: +2400 PLAN AT EL.: +4500 PLAN AT EL.: +5000 1

- ALLOWABLE DISPLACEMENT AND DEFLECTION: Vertical deflections: Design deflection of structural steel members, due to the sum of dead and live load, shall not exceed the following values: Load Combination:. Combo Name; Combo Type; Auto Design; Case Type; Case Name; Scale Factor; Steel Design. Def; Linear Add; No; Linear Static; DLs; 1; None. Def; Linear Static; EE; 1. Def; Linear Static; EO; 1. Def; Linear Static; L; 1. Floor beams supporting equipment: L/450 L=Span of the beam Max U3=0.72 mm ≤ 2400/450=5.33 mm

- Horizontal Deflections:

For Seismic condition (without contribution of other loads) (EQX, EQY)

11

According to: ASCE7-16 (TABLE 12.12-1): Risk Category: IV ⇒Allowable Drift = 0.015H

H = Height of the frame

H=5200mm;

Max U1=39.79 mm  ≤ 0.015*5200 =78 mm    Ok.

Max U2=4.17 mm  ≤ 0.015*5200 = 78 mm    Ok.

| TABLE: Joint Displacements |  |  |  |  |
| --- | --- | --- | --- | --- |
| Joint | OutputCase | CaseType | U1 | U2 |
| Text | Text | Text | mm | mm |
| 1 | ELX | LinStatic | 30.15 | 0.01 |
| 1 | ELY | LinStatic | 0.00 | 1.39 |
| 3 | ELX | LinStatic | 30.08 | 0.00 |
| 3 | ELY | LinStatic | 0.00 | 2.24 |
| 5 | ELX | LinStatic | 30.15 | -0.01 |
| 5 | ELY | LinStatic | 0.00 | 1.56 |
| 12 | ELX | LinStatic | 15.84 | 0.01 |
| 12 | ELY | LinStatic | 0.00 | 1.39 |
| 14 | ELX | LinStatic | 15.77 | 0.00 |
| 14 | ELY | LinStatic | 0.00 | 2.24 |
| 16 | ELX | LinStatic | 15.84 | -0.01 |
| 16 | ELY | LinStatic | 0.00 | 1.56 |
| 23 | ELX | LinStatic | 39.78 | 0.01 |
| 23 | ELY | LinStatic | 0.00 | 1.38 |
| 86 | ELX | LinStatic | 39.79 | 0.00 |
| 86 | ELY | LinStatic | 0.00 | 2.21 |
| 97 | ELX | LinStatic | 39.78 | -0.01 |
| 97 | ELY | LinStatic | 0.00 | 1.54 |
| 158 | ELX | LinStatic | 15.79 | 0.00 |
| 158 | ELY | LinStatic | 0.00 | 3.37 |
| 159 | ELX | LinStatic | 39.79 | 0.00 |
| 159 | ELY | LinStatic | 0.00 | 3.37 |
| 160 | ELX | LinStatic | 30.10 | 0.00 |
| 160 | ELY | LinStatic | 0.00 | 3.37 |
| 161 | ELX | LinStatic | 15.82 | -0.01 |
| 161 | ELY | LinStatic | 0.00 | 3.89 |
| 162 | ELX | LinStatic | 39.79 | -0.01 |
| 162 | ELY | LinStatic | 0.00 | 3.89 |
| 163 | ELX | LinStatic | 30.13 | -0.01 |
| 163 | ELY | LinStatic | 0.00 | 3.89 |
| 164 | ELX | LinStatic | 15.82 | 0.01 |
| 164 | ELY | LinStatic | 0.00 | 2.99 |
| 165 | ELX | LinStatic | 39.79 | 0.01 |
| 165 | ELY | LinStatic | 0.00 | 2.99 |
| 166 | ELX | LinStatic | 30.13 | 0.01 |
| 166 | ELY | LinStatic | 0.00 | 2.99 |
| 167 | ELX | LinStatic | 15.79 | 0.00 |
| 167 | ELY | LinStatic | 0.00 | 4.17 |
| 168 | ELX | LinStatic | 39.79 | 0.00 |
| 168 | ELY | LinStatic | 0.00 | 4.17 |
| 169 | ELX | LinStatic | 30.10 | 0.00 |
| 169 | ELY | LinStatic | 0.00 | 4.17 |