## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-ST-CN-0001_V00 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-SVTR-AA-0010 |  |  | Transmital Date:2025/01/11
Document Title: Steel Structure Calculation Books |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC- |  |  | Transmital Date:
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-ST-CN-0001_V00 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Sds=0.75 Sd1=0.41 Ss=1.125 S1=0.46 |  | BK-SUR-ENG-MEC-03-09216 | 2024-04-14 | -
2 | بار باد المان های فلزی اعمال گردد پیوست 6-4 |  | BK-SUR-ENG-MEC-03-09216 | 2024-04-14 | بار باد در نرم افزار به صورت Auto تعریف شد.
3 | بار باد مبحث ششم در سطح سرویس می باشد لذا در ترکیب بارها ضریب آن یک نمی باشد 1.6W |  |  |  | ترکیب بارها اصلاح گردید.
4 | kl/r=118 بادبندها |  |  |  | این کامنت شفاف نمی باشد.
5 | بیس پلیت ها و انکر بولت ها برای زلزله تشدید یافته طراحی گردد |  |  |  | بعد از تایید کلی دفترچه محاسباتی طراحی می گردد.
6 | F=RyfyAg نیروی طراحی اتصالات بادبندی |  |  |  | بعد از تایید کلی دفترچه محاسباتی طراحی می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: GH.KHOSRAVIZADEGAN | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 2024/04/14 |  |  |  |  | Date: