## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-AA-120-PR-DS-0001-V04 |  |  |  |  | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: Process Data Sheet for AE-2101 (A/B/C) |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-AA-0039 |  |  | Transmital Date: 2025/01/27
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-PR-DS-0001_V04 |  |  | CRS Status: | CM
| Comments (PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Process comments :
1 | مورد خاصی مطرح نمی باشد تنها مقدار توان فن ها با خروجی نرم افزار کمی اختلاف دارد. |  | BK-SUR-ENG-MEC-03-09814 | 2024-12-09 | لازم به توضیح است در فاینال بوک و با توجه به نهایی شدن مدرک فن، این موضوع اصلاح خواهد شد همچنین به استحضار می رساند: HTRI برنامه دقیقی برای انتخاب فن نمی باشد و فقط می توان محدوده توان فن انتخابی را بدست می آورد. توان فن ها به صورت اختصاصی در نرم افزار انتخاب فن (FAN Selection) بدست آمده است.
2 | سايز نازلهاي ابزار دقيق ميبايستي با الزامات پروژه همخواني داشته باشد. |  | BK-SUR-ENG-MEC-03-09814 | 2024-12-09 | سایز نازل ها ی ابزار دقیق مطابق با بخش INSTRUMENT مدرک (BK-GNRAL-PEDCO-000-IN-SP-0001_D04) اعمال شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.MALEKI/A.AHMADI | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 09/12/2024 |  |  |  |  | Date: