## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-AA-120-ME-DS-0001-V00 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-SVTR-AA-0038 |  |  | Transmital Date:2025/03/18
Document Title:FAN DATA SHEETS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC- |  |  | Transmital Date:
[5 empty] | CRS No:PEDCO-CRS-BK-GCS-AA-120-ME-DS-0001-V00 |  |  | CRS Status: | CM
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
AE-2101/AE-2102
1 | با توجه به اخرین ویرایش دیتا شیت فرآیندی (v04) تعداد blade ها 4 عدد در نظر گرفته شده که با این تعداد در دیتا شیت فن ها تناقض دارد. |  | BK-SUR-ENG-MEC-03-09889 | 2025-01-01 | Noted
1 | مطابق با بند 7.2.3.14 استانداردAPI 661 ضروریست الزامات اشاره شده در مورد فرکانس طبیعی blade ها مورد توجه و رعایت گردد |  | BK-SUR-ENG-MEC-03-09889 | 2025-01-01 | Noted
2 | نظر به اینکه ایرکولرها از نوع Induced Draft هستند، نسبت به Forced بودن فن های اشاره شده در دیتا شیت شفاف سازی گردد |  | BK-SUR-ENG-MEC-03-09889 | 2025-01-01 | Noted
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Al.Ahmadi | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 1/1/2025 |  |  |  |  | Date: