## Sheet1
ITEM | TAG NO. | EQUIPMENT DESIGNATION --- | STARTING MOTHOD | FAN Rotor Shaft Power | FAN Rotor Shaft Power @-15 Deg of Celsius | Mechanical Eff of Separated Power Transmission |  | Drive Rated Shaft Power @ Min Temp (5 Deg) | Drive Rated Shaft Power @ Max Temp (+55 Deg) | RATED VOLTAGE | Motor Output as per De-rating | MOTOR RATED POWER | SYNCHRON SPEED | MOTOR RATING | Conclusion
|  |  |  | (kW) | (kW) | N/A | B Type | (kW) | (kW) | (V) | (kW) |  | r.p.m
1 | AE-2101 A-B-C, | AIR COOLER | DOL | 3.15 | 3.84 | 0.95 | V BELTS | 4.24 | 3.46 | 400 | 5.5 * 0.89=4.8 | 5.5 | 1500 | 5.5 | Ok
2 | AE-2102 A-B-C, | AIR COOLER | DOL | 4.83 | 5.95 | 0.95 | V BELTS | 6.5 | 5.3 | 400 | 7.5 * 0.89=6.6 | 5.5 | 1500 | 7.5 | Ok