## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-PR-PI-0001 |  |  |  |  | Vendor Tr. N0:BK-HY-HD-T-0009 |  |  | Transmital Date:2023/05/28
Document Title: P&I DIAGRAMS |  |  |  |  | Client Tr. No:BK-HD-PEDCO-SVTR-HY-0003 |  |  | Transmital Date:2023/06/03
[5 empty] | CRS No:NISOC-CRS-BK-GCS-HY-120-PR-PI-0001-Rev(V00) |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت (DIRECTION) ورود و خروج سیگنال ها به/از MCC در نقشه نشان داده شود. |  | 02/2294/14506 | 1402/01/19 | مورد تایید است
2 | تگ های سیگنال ها درج گردد . به عنوان نمونه لازم است شماره اینترلاک هادر مدارک درج گردد. |  | 02/2294/14506 | 1402/01/19 | مورد تایید است
3 | ارتباطات UCP به DCS همچنین ارتباطات با ESD واحد نشان داده شود.سیمبل پنل های متفاوت نیز معرفی گردد. |  | 02/2294/14506 | 1402/01/19 | مورد تایید است
4 | به چه علت به موتورها MCC سیگنال ESD وارد نشده است؟آیا CAUSE توقف اضطراری برای ادوات وجود ندارد؟ |  | 02/2294/14506 | 1402/01/19 | به صورت کلی یک سیگنال ESD از کارفرما به UCP در نظر گرفته شده است و موجب shut down کمپرسور می گردد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: