## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-IN-DS-0005_V01
Document Title: CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-HY-0005 |  |  | Transmital Date:2023/08/28
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-IN-DS-0005_V00 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق اسناد پروژه Specification For Instrument and Control of Package Unit System (PU)براي پنل هاي داخل اتاق كنترل IP-54 در نظر گرفته شود. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | مورد تایید است مدرک اصلاح می گردد.
2 | تعداد UCP و پنل ها مشخص شود. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | تعداد تابلو در قسمت Dimensions موجود است.
3 | Hydrostat در نظر گرفته شود. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | مورد تایید است مدرک اصلاح می گردد.
4 | در خصوص ارتباط بين PLC ها شفاف سازي گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | با توجه به مستقل بودن سیستم کنترل کمپرسورها ، ارتباطی بین PLC ها وجود ندارد.
5 | مصارف الكتريكال ذكر گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | در مدرک ELECTRICAL/UPS CONSUMPTION LOAD LIST ارایه شده است
6 | تعداد CPU ها ذكر گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | در دیتاشیت مشخص شده است که CPU ها Redundant است.
7 | Certificate هايي كه ارائه مي شوند مشخص گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | Certificate مربوط SIL Relay & Barrier
8 | Licenseها ذكر گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | اضافه می گردد.
9 | با توجه به عنوان مدرك، مشخصات كنترل پنل هاي محلي هم ذكر گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | مشخصات LCP در مدرک ذیل ارایه می شود: LCP AND GAUGE BOARD LAYOUT BK-GCS-HY-120-IN-PY-0001
10 | در خصوص پنل IRP شفاف سازي گردد. |  | BK-SUR-ENG-MEC-02-07923 | 2023-06-20 | تابلوی IRP در اسکوپ هوایار نمی باشد
11 |  |  | س ط ب/5761 | 2023-06-26 | مورد تایید است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 20 Jun 2023 |  |  |  |  | Date: