## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-DS-0005
Document Title:CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO--SVTR-HY-0022 |  |  | Transmital Date:2023/10/22
[5 empty] | CRS No: NISOC-CRS-BK-GCS-HY-120-IN-LI-0005_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 02/2294/257669 | 1402/07/03 | تامین تابلو با ضخامت 3 میلیمتر برای درب ها امکان پذیر نیست. ماکزیمم ضخامت امکان پذیر 2.5mm می باشد. با توجه به محل نصب تابلو در ITR ضخامت ذکر شده را تایید فرمایید تا ما بتوانیم به مرحله تهیه مدارک Detail تابلو وارد شویم.
2 |  |  | 02/2294/257669 | 1402/07/03 | با Note اضافه می شود.
3 |  |  | 02/2294/257669 | 1402/07/03 | بریرهای استفاده شده برای سیستم ESD Relay base فاقد Hart support است. همچنین ترنسمیترهای Vibration نیز فاقد Hart هستند.همچنین برای سیستم ESD طبق توافق هدف مستقل کردن از سیستم کنترل بود لذا نیازی به Hart support بودن نمی باشد.
4 |  |  | 02/2294/257669 | 1402/07/03 | لیست نرم افزارها ارسال شده است.
5 |  |  | 02/2294/257669 | 1402/07/03 | اضافه می گردد.
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 17 Jul 2023 |  |  |  |  | Date: