## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-QC-PR-0003 | [5 empty] | EPC Contractor Tr. No.: |  |  | Transmital Date:
Document Title: SURFACE PREPARATION AND PAINTING PROCEDURE | [5 empty] | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-HY-0002 |  |  | Transmital Date:2023/11/28
[6 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-QC-PR-0003-V00 |  |  | CRS Status: | CM
Item | Comments (PEDCO) |  | Comments (By EPC Contractor) | Email/letter No. | Comment Date | Clarification (By Vendor) |  |  | Client Conclusion
1 | نام اعضا و نفراتي كه در برگيرنده prepared by/checked by/approved by هستند، بايد دقيق نوشته شود. از ذكر نام شركت جلوگيري شود.( كاور مدرك) |  | بازرسی تست های مورد نیاز به جدول 31 استاندارد IPS-E-TP-101 اشاره شود | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted. / Noted. Will be add as per added inspection test report
2 | در بند 6، جمله "except for staining. Random staining shall be limited to no more than 5 percent of each unit area of surface and may consist of light shadows, slight streaks, or minor discolorations caused by stains of rust, stains of mill scale, or stains of previously applied coating" حذف گردد. |  | به تميز كاري نواحي جوشها و اتصال جوشي و روش آن اشاره گردد | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted. / Noted.
3 | در دستورالعمل به مجاز نبودن استفاده از سيليس براي آماده سازي سطح مجاز اشاره گردد. در صورت استفاده از مسباره سايز دانه بندي مجاز مشخص گردد. |  | در سامانه رنگ لايه هاي متوالي رنگ بايد از نظر سايه رنگ و فام فرق داشته باشند. فام رنگ ها هر لایه مشخص گردد | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | اضافه می شود.، سایز مسباره 2mm می باشد و به دستورالعمل نیز اضافه می گردد. / به پروسیجر اضافه می گردد.
4 | در بند 7، منظور از جمله "While working, it should be visually confirmed whether the painting work instruction matches the paint colour or not." مشخص نميباشد. |  | در چک لیست بازرسی الزامات جدول 2 استاندارد IPS-C-TP-102(1) لحاظ گردد | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | This note will be deleted. / Noted. Will be add as per added inspection test report
5 | بندي تحت عنوان صلاحيت اپراتور رنگ آميزي اضافه گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | This Item is Not Applicable
6 | بندي تحت عنوان ابزار و تجهيزات مورد نياز جهت اجراي كار و انجام تستهاي مورد نياز اضافه گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted
7 | بندي تحت عنوان كاليبراسيون ابزار و تجهيزات اضافه گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted
8 | نحوه Mixing رنگ مشخص گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted.
9 | در بند 7، براي درصد ميزان رطوبت مجاز، دو عدد 80 و 85 درج شده كه ميبايست اصلاح گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted. Max will be 80%
10 | در بند 8.2، تنها روش مجاز رنگ آميزي، Air Less ميباشد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted.
11 | در فرمت بازرسي آماده سازي سطح و رنگ آميزي، تماي پارامترهايي كه ميبايست تحت كنترل باشند، از جمله كنترل شرايط محيطي (دما، رطوبت و ...)، زبري سطح، تست چسبندگي و ساير تستهاي مورد نياز درج گردد. همچنين محل امضا در فرمت، متناسب با پارتيهاي تعريف شده در ITP مصوب اصلاح گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted
12 | شركت سازنده رنگ ميبايست از سازندگان مجاز (AVL) انتخاب گردد. همچنين به لزوم يكسان بودن سازنده رنگ لايه هاي مختلف اشاره گردد. |  |  | BK-SUR-ENG-QAC-02-07809 | 2023-06-06 | Noted.
14
15
16
17
18
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) | [5 empty] | EPC Contractor
| Commented By: Y.Norouzian | Signature |  |  |  |  | Clarified By: M.Kamal | Signature
| Date: 06-06-23 | [5 empty] | Date: