## Cover
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [8 empty] | شماره صفحه: 1 از 42
[5 empty] | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه
[5 empty] | BK | GCS | HY |  | 120 | IN | DS | 0001 | V02
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT DATASHEETS / CERTIFICATES نگهداشت و افزایش تولید میدان نفتی بینک
V02 | Dec..2023 |  |  | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | S.Faramarzpour
V01 | Nov.2023 |  |  | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | S.Faramarzpour
V00 | SEP.2023 |  |  | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | M.Mehrshad
Rev. | Date |  |  | Purpose of Issue/Status |  |  |  | Prepared By |  |  | Checked By |  |  |  | Approved By | Client Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR:Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Rev
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 2 از 42
[5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | HY | 120 | IN | DS |  | 0001 |  | V02
REVISION RECORD SHEET
| Page | V00 | V01 | V02 |  | V03 |  | V04 |  |  | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | X | X | X | [6 empty] | 1
| 2 | X | X | X | [6 empty] | 2
| 3 | X | X | X | [6 empty] | 3
| 4 | X | X | X | [6 empty] | 4
| 5 | X | X | X | [6 empty] | 5
| 6 | X | X | X | [6 empty] | 6
| 7 | X | X | X | [6 empty] | 7
| 8 | X | X | X | [6 empty] | 8
| 9 | X | X | X | [6 empty] | 9
| 10 | X | X | X | [6 empty] | 10
| 11 | X | X | X | [6 empty] | 11
| 12 | X | X | X | [6 empty] | 12
| 13 | X | X | X | [6 empty] | 13
| 14 | X | X | X | [6 empty] | 14
| 15 | X | X | X | [6 empty] | 15
| 16 | X | X | X | [6 empty] | 16
| 17 | X | X | X | [6 empty] | 17
| 18 | X | X | X | [6 empty] | 18
| 19 | X | X | X | [6 empty] | 19
| 20 | X | X | X | [6 empty] | 20
| 21 | X | X | X | [6 empty] | 21
| 22 | X | X | X | [6 empty] | 22
| 23 | X | X | X | [6 empty] | 23
| 24 | X | X | X | [6 empty] | 24
| 25 | X | X | X | [6 empty] | 25
| 26 | X | X | X | [6 empty] | 26
| 27 | X | X | X | [6 empty] | 27
| 28 | X | X | X | [6 empty] | 28
| 29 | X | X | X | [6 empty] | 29
| 30 | X | X | X | [6 empty] | 30
| 31 | X | X | X | [6 empty] | 31
| 32 | X | X | X | [6 empty] | 32
| 33 | X | X | X | [6 empty] | 33
| 34 | X | X | X | [6 empty] | 34
| 35 | X | X | X | [6 empty] | 35
| 36 | X | X | X | [6 empty] | 36
| 37 | X | X | X | [6 empty] | 37
| 38 | X | X | X | [6 empty] | 38
| 39 | X | X | X | [6 empty] | 39
| 40 | X | X | X | [6 empty] | 40
| 41 | X | X | X | [6 empty] | 41
| 42 |  |  | X | [6 empty] | 42
| 43 | [9 empty] | 43
| 44 | [9 empty] | 44

## Content
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [10 empty] | شماره صفحه: 3 از 42
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
|  |  | BK |  | GCS | HY | 120 | IN | DS |  | 0001 |  | V02
Table of Content
| Page | Content | [5 empty] | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | Cover | [5 empty] | 1
| 2 | Revised Pages | [5 empty] | 2
| 3 | Table of Content | [5 empty] | 3
| 4 | Pressure Gauge | [5 empty] | 4
| 5 | Pressure trasmitter data sheet | [5 empty] | 5
| 6 | Pressure trasmitter List | [5 empty] | 6
| 7 | Tempearture Gauge | [5 empty] | 7
| 8 | Tempearture Trasmitter data sheet | [5 empty] | 8
| 9 | Tempearture Trasmitter List | [5 empty] | 9
| 10 | Diff Pressure trasmitter data sheet | [5 empty] | 10
| 11 | Diff Pressure trasmitter List | [5 empty] | 11
| 12 | Diff Pressure Gauge data sheet | [5 empty] | 12
| 13 | Flow indicator Comp C-2101A | [5 empty] | 13
| 14 | Flow indicator Comp C-2101B | [5 empty] | 14
| 15 | Flow indicator Comp C-2101C | [5 empty] | 15
| 16 | Sight Glass data sheet | [5 empty] | 16
| 17 | Sight Glass data List | [5 empty] | 17
| 18 | Flow transmitter 2121A | [5 empty] | 18
| 19 | Flow transmitter 2131A | [5 empty] | 19
| 20 | Flow transmitter C-2206A | [5 empty] | 20
| 21 | Flow transmitter 2121B | [5 empty] | 21
| 22 | Flow transmitter 2131B | [5 empty] | 22
| 23 | Flow transmitter C-2206B | [5 empty] | 23
| 24 | Flow transmitter 2121C | [5 empty] | 24
| 25 | Flow transmitter 2131C | [5 empty] | 25
| 26 | Flow transmitter C-2206C | [5 empty] | 26
| 27 | Level gauge C-LG-2213A | [5 empty] | 27
| 28 | Level gauge C-LG-2213B | [5 empty] | 28
| 29 | Level gauge C-LG-2213C | [5 empty] | 29
| 30 | Level Transmitter C-LT-2213A | [5 empty] | 30
| 31 | Level Transmitter C-LT-2213B | [5 empty] | 31
| 32 | Level Transmitter C-LT-2213C | [5 empty] | 32
| 33 | Solenoid Data sheet | [5 empty] | 33
| 34 | Solenoid List | [5 empty] | 34
| 35 | Vibration & rod drop data sheet C-2101A | [5 empty] | 35
| 36 | Vibration & rod drop data sheet C-2101B | [5 empty] | 36
| 37 | Vibration & rod drop data sheet C-2101C | [5 empty] | 37
| 38 | Level Transmitter C-LT-2200A | [5 empty] | 38
| 39 | Level Transmitter C-LT-2200B | [5 empty] | 39
| 40 | Level Transmitter C-LT-2200C | [5 empty] | 40
| 41 | Pressure switch data Sheet | [5 empty] | 41
| 42 | Temp switch data Sheet | [5 empty] | 42
| 43 | [6 empty] | 43
| 44 | [6 empty] | 44

## PG
NISOC | [8 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 | [8 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [20 empty] | شماره صفحه: 4 از 42
[9 empty] | پروژه |  |  |  | بسته کاری |  | صادرکننده | تسهیلات |  |  | رشته |  |  | نوع مدرک |  |  |  | سریال |  |  | نسخه
[9 empty] | BK |  |  |  | GCS |  | HY | 120 |  |  | IN |  |  | DS |  |  |  | 0001 |  |  | V02
Data Sheet for Pressure Gauge
1 | Type : | Direct Rdg. | [5 empty] | 3-15 lb Reciever | [7 empty] | 11 | MFR.& Model No. | [6 empty] | SANGAN PG-20
|  | Other | liquid filled | [12 empty] | 12 | Press Element : Bourdon | [10 empty] | Bellows
2 | Mounting : | Surface |  |  | Local | [5 empty] | Flush | [11 empty] | Other
3 | Dial : | Diameter |  | 160 mm |  |  | Color : White / Black Lettering ,Aluminum Non Rusting Metal | [8 empty] | 13 | Element Mtl. : | [5 empty] | Bronze |  |  |  | Steel
4 | Case : | Cast Iron |  |  |  |  | S.S |  |  |  |  | Phenol | [7 empty] | SS |  |  | Other |  | 316SS
|  | Other | [13 empty] | 14 | Socket Mtl. : | [5 empty] | Bronze |  |  |  | Steel
5 | Ring : | Screwed |  |  | Hinged | [6 empty] | Slip | [7 empty] | SS |  |  | Other |  | 316SS
|  | Std |  |  | Other | [10 empty] | 15 | Connection-NPT : | [5 empty] | 1/4 in. |  |  |  | 1/2 in. |  |  |  | Other | NPTM (refer to note)
6 | Blow-out Protection : |  |  |  | None |  |  |  |  | Back |  |  | Disc | [9 empty] | Bottom |  |  |  | Back
|  | Solid Front | [6 empty] | Other | [6 empty] | 16 | Movement: | [5 empty] | Bronze |  |  |  | SS
7 | Lens : | Glass |  |  | Plastic |  |  |  | Safety Glass ( shatter proof) | [11 empty] | Naylon |  |  |  |  | Other |  |  |  | Stainless Steel
8 | Options : | [14 empty] | 17 | Diaphragm Seal |  |  |  | As per List
[10 empty] | As per List | [8 empty] | MFR. | [9 empty] | Type
[19 empty] | Wetted Part Mtl. | [9 empty] | Other Mtl.
Fill Fluid :
9 | Nominal Accuracy Required : |  |  |  |  | ± 0.5% of full scale | [12 empty] | Process Conn. :
10 | Over range protection : |  |  | 1.3 times the maximum scale reading | [11 empty] | 18 | Ingress Protection : | [5 empty] | IP 65
[16 empty] | 19 | Manifold S.S316 2 valve
Item | Tag No. |  | Range (barg) |  |  |  | Process Fluid/State | Design | [5 empty] | Operating |  |  |  | LINE NO./EQUIPMENTNO. | [7 empty] | P&ID NO. | [6 empty] | Accessories | NOTE
[8 empty] | Press (barg) |  |  |  | Temp (C°) |  | Press (barg) |  | Temp (C°)
1 | C-PG-2190A |  | 0-10 |  |  |  | Process gas Comp A | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 10 barg
2 | C-PG-2191A |  | 0-40 |  |  |  | Process gas Comp A | 24.5 |  |  |  | 180 |  | 18 |  | 129 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
3 | C-PG-2193A |  | 0-40 |  |  |  | Process gas Comp A | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 40 barg
4 | C-PG-2194A |  | 0-100 |  |  |  | Process gas Comp A | 62 |  |  |  | 180 |  | 54.9 |  | 148 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Cooling Element Nace material
5 | C-PG-2200A |  | 0-16 |  |  |  | Instrument Air Comp A | 12.5 |  |  |  | 85 |  | 8 |  | 65 |  | ISA-112-0002A-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2
6 | C-PG-2201A |  | 0-16 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0004A-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
7 | C-PG-2202A |  | 0-16 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0003A-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
8 | C-PG-2204A |  | 0-16 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 6 |  | 60 |  | OIL-112-0008A-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
9 | C-PG-2205A |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009A-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
10 | C-PG-2206A |  | 0-6 |  |  |  | Water console Comp A | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0003A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
11 | C-PG-2207A |  | 0-6 |  |  |  | Water console Comp A | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0004A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
12 | C-PG-2208A |  | 0-6 |  |  |  | Water console Comp A | 7 |  |  |  | 85 |  | 3 |  | 58 |  | CWS-112-0002A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5
13 | C-PG-2190B |  | 0-10 |  |  |  | Process gas Comp B | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 10barg
14 | C-PG-2191B |  | 0-40 |  |  |  | Process gas Comp B | 24.5 |  |  |  | 180 |  | 18 |  | 129 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
15 | C-PG-2193B |  | 0-40 |  |  |  | Process gas Comp B | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 40 barg
16 | C-PG-2194B |  | 0-100 |  |  |  | Process gas Comp B | 62 |  |  |  | 180 |  | 54.9 |  | 148 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Cooling Element Nace material
17 | C-PG-2200B |  | 0-16 |  |  |  | Instrument Air Comp B | 12.5 |  |  |  | 85 |  | 8 |  | 65 |  | ISA-112-0002A-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2
18 | C-PG-2201B |  | 0-16 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0004A-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
19 | C-PG-2202B |  | 0-16 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0003A-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
20 | C-PG-2204B |  | 0-16 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 6 |  | 60 |  | OIL-112-0008A-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
21 | C-PG-2205B |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009A-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
22 | C-PG-2206B |  | 0-6 |  |  |  | Water console Comp B | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0003A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
23 | C-PG-2207B |  | 0-6 |  |  |  | Water console Comp B | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0004A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
24 | C-PG-2208B |  | 0-6 |  |  |  | Water console Comp B | 7 |  |  |  | 85 |  | 3 |  | 58 |  | CWS-112-0002A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5
25 | C-PG-2190C |  | 0-10 |  |  |  | Process gas Comp C | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 10barg
26 | C-PG-2191C |  | 0-40 |  |  |  | Process gas Comp C | 24.5 |  |  |  | 180 |  | 18 |  | 129 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
27 | C-PG-2193C |  | 0-40 |  |  |  | Process gas Comp C | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material Over protectior Snubber Set point 40 barg
28 | C-PG-2194C |  | 0-100 |  |  |  | Process gas Comp C | 62 |  |  |  | 180 |  | 54.9 |  | 148 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Cooling Element Nace material
29 | C-PG-2200C |  | 0-16 |  |  |  | Instrument Air Comp C | 12.5 |  |  |  | 85 |  | 8 |  | 65 |  | ISA-112-0002A-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2
30 | C-PG-2201C |  | 0-16 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0004A-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
31 | C-PG-2202C |  | 0-16 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 6 |  | 70 |  | OIL-112-0003A-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
32 | C-PG-2204C |  | 0-16 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 6 |  | 60 |  | OIL-112-0008A-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3
33 | C-PG-2205C |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009A-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1 | [6 empty] | Nace material
34 | C-PG-2206C |  | 0-6 |  |  |  | Water console Comp C | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0003A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
35 | C-PG-2207C |  | 0-6 |  |  |  | Water console Comp C | 7 |  |  |  | 85 |  | 3 |  | 65 |  | CWS-112-0004A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5 | [6 empty] | Pulsation Damper (Snubber)
36 | C-PG-2208C |  | 0-6 |  |  |  | Water console Comp C | 7 |  |  |  | 85 |  | 3 |  | 58 |  | CWS-112-0002A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5

## PT
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 5 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V02
Data Sheet for Pressure Transmitter
| 1 | Tag No.: (Refer to Next Page) | Service: (Refer to Next Page)
GENERAL | 2 | Function | Recordo Indicaten Controlo Blindo Transn Intego (Note1)
| 3 | Case | MFR STDn Nom Sizeo Color MFR STDn Other
| 4 | Mounting | Flusho Surfaceo Yoken Other
| 5 | Enclosure Class | General Purposeo Weather Proof n Explosion-Proof o Class
|  |  | For use in Intrinsically Safe Systemn | [5 empty] | Other EExia, IIB, T4
| 6 |  | Ingress Protection : IP 66
| 7 | Power Supply | 117 V 60 Hzo Other: aco dcn Volts : 24 VDC Loop Powered
TRANSMITTER | 8 | Trans. Output | 4-20mAn 10-50mAo 21-10 kpa(3-15 psig)o Other 4-20mA Smart HART
| 9 |  | Transmitter Accuracy : 0.1% of full scale.
UNIT | 10 | Service | Gage Press n Vacuumo Absoluteo Compound o
| 11 | Element Type | Diaphragmn Helixo Bourdon o Bellowso Fill Fluid:Silicone
| 12 | Material | Body Aluminum Element 316 S.S. as minimum
| 13 | Range | Fixedo Adj. Range n Set At (Refer to Next Page)
| 14 | Rating | Overrange Protection: at least 1.5 times the maximum range
| 15 | Process Data | Press: Normal Max Element Range (Refer to Next Page)
| 16 | Process Conn. | ½ in. NPTn Other Male with wrench flats
| 17 |  | Location: Bottom n Back o Other
| 18 | Electrical Conn. | MFR STDo Other ISO M20x1.5
OPTIONS | 19 | Miscellaneous | Filt Reg.o Sup. Gageo Output Gageo Charts
| 20 | Diaphragm Seal | Diaph Seal o Type : Capillary Length: Mtl. :
Conn. Fill Fluid : shall be Suitable for Normal and Max. Operating Temp
Flushing Connection :
| 21 | Manifold | Valve Manifold : See list
| 22 | MFR. & Model No. | See PT list
Notes:
1- All transmitters shall be provided complete with LCD type integral indicator .
2- Repeatability of the transmitter shall be better than 0.1% of the span.
3- All transmitters shall be reverse polarity protected.
4- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
5- NACE MR-01-75 to be considered.

## PT List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 42
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V02
List of PT
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | VISCOSITY (cP) | CALIBRATED RANGE (Barg) | ACCESSORIES Option | MFR. & Model No. | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Norm. / Design | VISCOSITY (Cst) |  | ACCESSORIES | ACCESSORIES | REV. Remark
1 | PT-2123A | Process gas Comp A | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.0115 | 0-16 | Nace material 2 valve manifold S.S316 |  | Loose Item
2 | C-PT-2133A | Process gas Comp A | GAS-111-0051A-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 54.9 / 62 | 148 / 180 | 0.0164 | 0-65 | Nace material 2 valve manifold S.S316
3 | PT-2124A | Process gas Comp A | GAS-111-0036A-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 18 / 24.5 | 129 / 180 | 0.0149 | 0-30 | Nace material 2 valve manifold S.S316 |  | Loose Item
4 | PT-2132A | Process gas Comp A | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.0126 | 0-25 | Nace material 2 valve manifold S.S316 |  | Loose Item
5 | C-PT-2201A | Instrument Air Comp A | ISA-112-0002A-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2 | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316
6 | C-PT-2200A | Lubricator Comp A | OIL-112-0008A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316
7 | C-PT-2204A | Lube Oil Comp A | OIL-112-0008A-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3 | 1" NPT | Liquid | 6 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316
8 | C-PT-2210A | N2 Gas Supply Comp A | NIT-112-0001A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 2.2 / 10 | 60 / 85 | 0.0199 | 0-4 | 2 valve manifold S.S316
9 | C-PT-2211A | N2 Gas Supply Comp A | NIT-112-0002A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 1 / 10 | 60 / 85 | 0.0198 | 0-2 | 2 valve manifold S.S316
10 | C-PT-2220A | Water console Comp A | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316
11 | C-PT-2221A | Water console Comp A | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316
12 | PT-2123B | Process gas Comp B | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.0115 | 0-16 | Nace material 2 valve manifold S.S316 |  | Loose Item
13 | C-PT-2133B | Process gas Comp B | GAS-111-0051A-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 54.9 / 62 | 148 / 180 | 0.0164 | 0-65 | Nace material 2 valve manifold S.S316
14 | PT-2124B | Process gas Comp B | GAS-111-0036A-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 18 / 24.5 | 129 / 180 | 0.0149 | 0-30 | Nace material 2 valve manifold S.S316 |  | Loose Item
15 | PT-2132B | Process gas Comp B | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.0126 | 0-25 | Nace material 2 valve manifold S.S316 |  | Loose Item
16 | C-PT-2201B | Instrument Air Comp B | ISA-112-0002A-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2 | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316
17 | C-PT-2200B | Lubricator Comp B | OIL-112-0008A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316
18 | C-PT-2204B | Lube Oil Comp B | OIL-112-0008A-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3 | 1" NPT | Liquid | 6 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316
19 | C-PT-2210B | N2 Gas Supply Comp B | NIT-112-0001A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 2.2 / 10 | 60 / 85 | 0.0199 | 0-4 | 2 valve manifold S.S316
20 | C-PT-2211B | N2 Gas Supply Comp B | NIT-112-0002A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 1 / 10 | 60 / 85 | 0.0198 | 0-2 | 2 valve manifold S.S316
21 | C-PT-2220B | Water console Comp B | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316
22 | C-PT-2221B | Water console Comp B | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316
23 | PT-2123C | Process gas Comp C | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.0115 | 0-16 | Nace material 2 valve manifold S.S316 |  | Loose Item
24 | C-PT-2133C | Process gas Comp C | GAS-111-0051A-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | S | 148 / 180 | 0.0164 | 0-65 | Nace material 2 valve manifold S.S316
25 | PT-2124C | Process gas Comp C | GAS-111-0036A-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 18 / 24.5 | 129 / 180 | 0.0149 | 0-30 | Nace material 2 valve manifold S.S316 |  | Loose Item
26 | PT-2132 | Process gas Comp C | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.0126 | 0-25 | Nace material 2 valve manifold S.S316 |  | Loose Item
27 | C-PT-2201C | Instrument Air Comp C | ISA-112-0002A-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2 | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316
28 | C-PT-2200C | Lubricator Comp C | OIL-112-0008A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316
29 | C-PT-2204C | Lube Oil Comp C | OIL-112-0008A-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3 | 1" NPT | Liquid | 6 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316
30 | C-PT-2210C | N2 Gas Supply Comp C | NIT-112-0001A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 2.2 / 10 | 60 / 85 | 0.0199 | 0-4 | 2 valve manifold S.S316
31 | C-PT-2211C | N2 Gas Supply Comp C | NIT-112-0002A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4 | 1" NPT | Gas | 1 / 10 | 60 / 85 | 0.0198 | 0-2 | 2 valve manifold S.S316
32 | C-PT-2220C | Water console Comp C | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316
33 | C-PT-2221C | Water console Comp C | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5 | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-6 | 2 valve manifold S.S316

## TEMPERATURE GAUGE(BIMETAL)
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | پروژه |  |  | بسته کاری |  | صادر کننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 7 از 42
[5 empty] | BK |  |  | GCS |  | HY |  | 120 |  | IN | DS |  | 0001 |  | V02
BI-METALLIC THERMOMETER WITH WELL (Complete Assembly)
| THERMOMETER | [14 empty] | WELL
1 | ELEMENT TYPE |  | BI-METAL ■ |  |  |  |  | GAS FILLED CAPILLARY □ | [6 empty] | 15 | NONE □ |  |  |  |  | INCLUDED ■
2 | STEM | THREADED (NPTM) ■ |  |  |  | UNION □ |  |  |  |  | PLAIN □ |  |  |  | 16 | MATERIAL : |  |  |  | 304 SS □ |  | 316 SS ■ |  | OTHER
| MATERIAL |  | S.S | [11 empty] | 17 | CONSTRUCTION |  |  |  |  | BUILT-UP □ |  | DRILLED BAR STOCK ■
3 | STEM OR UNION THREADED : | [5 empty] | 1/2 IN. ■ |  |  |  | 3/4 IN. □ | [9 empty] | OTHER
4 | STEM DIAMETER |  |  |  | MFR. STD □ |  |  | 6 mm. ■ |  |  |  |  | 8 mm. □ | [7 empty] | TAPERED ■ |  | STRAIGHT □
5 | CASE MATERIAL : |  |  |  | MFR. STD □ |  |  |  | OTHER |  | S.S |  |  |  | 18 | INTERNAL CONNECTION NOMINAL SIZE | [6 empty] | 1/2" PIPE THREAD
6 | DIAL : | SIZE |  | 160 mm |  |  |  | COLOR |  | White / Black Lettering Aluminum,Non Rusting Metal |  |  |  |  | 19
7 | SCALE TYPE : |  | °C |  |  |  | POINTER ADJUSTMENT | [5 empty] | YES |  | 20
8 | SCALE LENGTH : |  |  | MFR. STD. |  |  |  | COLOR |  | MFR.STD |  |  |  |  | 21
9 | FORM : |  | FIG NO. |  | EVERY ANGLE | [9 empty] | 22 | FLANGE RATING |  |  |  | REFER TO BELOW TABLE
10 | EXTERNAL CALIBRATOR ■ | [6 empty] | `
11 | PROTECTION CLASS : |  |  |  | IP65 | [9 empty] | 23 | MANUFACTURER |  |  |  | SANGAN
12 | ACCURACY : |  |  |  | ±1 % OF FULL SCALE RANGE | [9 empty] | 24 | MODEL NO. |  |  |  | TE18
13 | WINDOW MATERIAL : |  | SHATTER PROOF TYPE
14 | RING TYPE/MATERIAL : |  |  |  | SCREWED/S.S316
ITEM NO. | TAG NO. | LINE SIZE | WELL "U" mm (*) (NOTE 1) |  |  | STEM LENGTH (mm) (*) |  | OPER. TEMP. (°C) |  | DESIGN TEMP.(°C)/ PRESSURE (BARG) |  | RANGE (°C) |  | PRESSURE (barg) Norm./ Max. | PROCESS/WELL CONNECTION & RATING (ANSI) |  |  | Max. VELOCITY (cP) |  |  | SERVICE |  |  | P&ID NO. | NOTES
1 | C-TG-2190A | 1ST STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 36.8 |  | 180 / 24.5 |  | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Thermowell Nace
2 | C-TG-2193A | 2nd STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 59.9 |  | 180 / 62 |  | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Thermowell Nace
3 | C-TG-2204A | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
4 | C-TG-2205A | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
5 | C-TG-2206A | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 70 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
6 | C-TG-2210A | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
7 | C-TG-2211A | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
8 | C-TG-2217A | Water Reservoir | Hold |  |  | 200 |  | 65 |  | 85 / 3.5 |  | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
9 | C-TG-2221A | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
10 | C-TG-2215A | 1" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
11 | C-TG-2216A | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
12 | C-TG-2212A | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 58 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
13 | C-TG-2213A | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
14 | C-TG-2214A | 2'1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
15 | C-TG-2190B | 1ST STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 36.8 |  | 180 / 24.5 |  | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Thermowell Nace
16 | C-TG-2193B | 2nd STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 59.9 |  | 180 / 62 |  | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
17 | C-TG-2204B | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
18 | C-TG-2205B | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
19 | C-TG-2206B | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 70 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
20 | C-TG-2210B | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
21 | C-TG-2211B | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
22 | C-TG-2217B | Water Reservoir | Hold |  |  | 200 |  | 65 |  | 85 / 3.5 |  | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
23 | C-TG-2221B | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
24 | C-TG-2215B | 1" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
25 | C-TG-2216B | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
26 | C-TG-2212B | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 58 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
27 | C-TG-2213B | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
28 | C-TG-2214B | 2'1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
29 | C-TG-2190C | 1ST STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 36.8 |  | 180 / 24.5 |  | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Thermowell Nace
30 | C-TG-2193C | 2nd STAGE SUCTION SNUBBER | 400 |  |  | 450 |  | 59.9 |  | 180 / 62 |  | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Thermowell Nace
31 | C-TG-2204C | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
32 | C-TG-2205C | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
33 | C-TG-2206C | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 70 |  | 85 / 10 |  | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
34 | C-TG-2210C | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
35 | C-TG-2211C | 2" TO 4" (Expanded) | 150 |  |  | 200 |  | 60 |  | 85 / 5 |  | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page4 | Thermowell Nace
36 | C-TG-2217C | Water Reservoir | Hold |  |  | 200 |  | 65 |  | 85 / 3.5 |  | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
37 | C-TG-2221C | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
38 | C-TG-2215C | 1" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
39 | C-TG-2216C | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
40 | C-TG-2212C | 3" TO 4" (Expanded) | 150 |  |  | 200 |  | 58 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
41 | C-TG-2213C | 1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
42 | C-TG-2214C | 2'1/2" TO 4" (Expanded) | 150 |  |  | 200 |  | 65 |  | 85 / 7 |  | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6

## TT
NISOC |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  |  | پروژه |  | بسته کاری |  | صادر کننده |  | تسهیلات |  | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 42
|  |  |  | BK |  | GCS |  | HY |  | 120 |  | IN | DS | 0001 |  | V02
Data Sheet for Temprarure Transmitter/Element/Thermowell
| HEAD | [12 empty] | 21 | BORE DIAMETER 6.6 mm (NOTE 4)
1 | COMPLETE ASSEMBLY |  |  |  | YES |  | OTHER | [6 empty] | 22 | OUTSIDE DIAMETER AT SUPPORT/TIP : 28/22 mm (NOTE 4)
2 | SCREWED COVER ■ |  |  |  |  | OTHER | [7 empty] | 23 | LAGGING EXTENTION "T" : VTA
3 | PROTECTION CLASS |  |  |  | IP-66 | [8 empty] | 24 | TEST : HYDROSTATIC AND PENETRANT TEST
4 | HAZ. AREA CLASSIFICATION |  |  |  | EXia IIB T4 | [8 empty] | 25 | CONNECTION TO SENSOR |  |  |  |  | 1/2" NPT F
5 | MATERIAL | 316 S.S |  |  | ELECTRICAL CONN. | [5 empty] | M20 X 1.5 |  |  | 26 | PROCESS CONNECTION |  |  |  | See list
6 | NIPPLE SIZE | 1/2" |  |  | DIM."N" | [5 empty] | UNION □
7 | AMBIENT TEMPERATURE IN DIRECT SUNLIGHT | [13 empty] | PERFORMANCE CHARACTERISTICS
| ELEMENT | [12 empty] | 27 | MIN/MAX. AMBIENT WORKING TEMPERATURE: | [6 empty] | BY VENDOR
8 | PLATINUM ■ 100/0°C |  | NICKEL □ |  |  |  |  | OTHER
9 | TYPE |  | PT100 | [11 empty] | TRANSMITTER
10 | TEMPERATURE RANGE |  |  | -100ºC to 500 ºC | [9 empty] | 28 | TRANSMITTER BODY MATERIAL |  |  |  |  | EXOPXY PAINTED DIE CAST ALUMINIUM
11 | LEADS | STD □ |  |  | POTTED □ |  |  |  |  | HERM. SEALED ■ |  |  |  | 29 | POWER SUPPLY | [5 empty] | 24 VDC, LOOP POWERED WITH HART
12 | SHEAT MATERIAL |  | 316 S.S. |  |  | O.D. |  |  |  | 6 mm |  |  |  | 30 | OUTPUT RANGE | [5 empty] | 4-20 ma
13 | TYPE | SINGLE ■ |  |  |  | DUPLEX □ | [7 empty] | 31 | TRANSMITTER MOUNTING | [5 empty] | HEAD MOUNTED
14 | SPRING LOADED |  |  | YES ■ |  |  | NO □ | [6 empty] | 32 | ELECTRICAL CONNECTION | [5 empty] | ISO M20
15 | CONNECTION | 2-WIRE □ |  |  | 3-WIRE ■ |  |  | 4-WIRE □ | [5 empty] | 33 | ACCURACY |  |  | ± 0.1 % OF CALIBRATED SPAN
16 | LEAD WIRES ■ |  | RECEPTACLE □ | [5 empty] | TERMINAL BLOCK ■ |  |  |  |  | 34 | ENCLOSURE APPROVAL | [5 empty] | ATEX
| OTHER | [12 empty] | 35 | ZERO ADJUST: YES SPAN ADJUST:YES
| WELL OR TUBE | [12 empty] | 36 | ISOLATION TYPE: Barier
17 | NONE □ INCLUDE ■ BY OTHERS □ | [12 empty] | 37 | NIPPLE & UNION MATERIAL: S.S
18 | MATERIAL |  | AISI 316 S.S. | [10 empty] | 38 | LCD INDICATOR: YES
19 | CONSTRUCTION |  | TAPERED ■ |  |  |  |  | STRAIGHT □ | [5 empty] | 39 | MANUFACTURER: * |  | See list |  |  | MODEL NO. : See list
20 | SOILD BAR-STOCK ■ |  |  | BUILT-UP □ |  |  |  | CLOSE-END TUBE □
NOTES :
* VENDOR TO CONFIRM
1) VENDOR SHALL FULLY SUPPLY & ASSEMBLE THERMOWELL WITH THERMOELEMENT AND HEAD MOUNTED TRANSMITTER.
2) SURFACE TEMPERATURE WILL REACH TO 85˚C IN EXPOSURE OF DIRECT SUNLIGHT.
3) HEAD COVER SHALL BE FRONT GLASS TYPE FOR COMPATIBILITY OF INDICATOR REQUIREMENT
4)WAKE FREQUENCY CALCULATION SHALL BE SUBMITTED BY MANUFACTURE FOR FINALIZING ALL THERMOWELL SIZE. (ASME PTC 19.3)
5)THE LINE SIZE SHALL BE EXPANDED TO 4".
6)REFER TO IPS-D-IN-101" FOR THERMOWELL DIMENSION.
7)COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## TT List
NISOC | [6 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
شماره پیمان: 9184 – 073 - 053 | [6 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 9 از 42
[7 empty] | پروژه |  | بسته کاری |  | صادر کننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه
[7 empty] | BK |  | GCS |  | HY | 120 | IN |  | DS | 0001 |  | V02
List of TT/TE/TW
ITEM NO. | TAG NO. | LINE SIZE | WELL DIMENTION (mm) (*) |  | OPER. TEMP. (°C) | DESIGN TEMP.(°C) |  | MAX VELOCITY (m/s) |  | RANGE (°C) | PRESSURE Nor./Des. (barg) | PROCESS CONNECTION & RATING (ANSI) |  | INDICATOR | TRANSMITTER MOUNTING |  | SERVICE |  |  | P&ID NO. | MFR. & Model No. | NOTES
|  |  | U | STEM
1 | TT-2122A | 8" | 250 | 290 | 36.8 | 180 |  | 9 |  | 0-100 | 4.9 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0031A-AN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
2 | C-TT-2191A | _ | 400 | 450 | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | Process Gas 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Thermowell Nace
3 | TT-2123A | 6" | 250 | 290 | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
4 | TT-2132A | 6" | 200 | 240 | 59.9 | 180 |  | 8 |  | 0-120 | 17.1 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
5 | TT-2133A | 6" | 200 | 240 | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
6 | C-TT-2194A | _ | 400 | 450 | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | Process Gas 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
7 | C-TT-2204A | 2" TO 4" (Expanded) | 150 | 200 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
8 | C-TT-2203A | _ | 200 | 250 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase CompA |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
9 | C-TT-2213A | _ | HOLD | HOLD | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
10 | C-TT-2214A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
11 | C-TT-2215A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
12 | C-TT-2216A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
13 | C-TT-2218A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
14 | C-TT-2217A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
15 | C-TT-2219A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
16 | C-TT-2220A | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
17 | TE-2222A TE-2223A TE-2224A | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
18 | TE-2225A TE-2226A TE-2227A | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
19 | TE-2228A TE-2229A TE-2230A | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
20 | TT-2122B | 8" | 250 | 290 | 36.8 | 180 |  | 9 |  | 0-100 | 4.9 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | GAS-111-0031A-AN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
21 | C-TT-2191B | _ | 400 | 450 | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Thermowell Nace
22 | TT-2123B | 6" | 250 | 290 | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
23 | TT-2197B | 6" | 200 | 240 | 59.9 | 180 |  | 8 |  | 0-120 | 17.1 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
24 | TT-2123B | 6" | 200 | 240 | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | REMOTE TYPE |  | GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
25 | C-TT-2194B | _ | 400 | 450 | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
26 | C-TT-2204B | 2" TO 4" (Expanded) | 150 | 200 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
27 | C-TT-2203B | _ | 200 | 250 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase CompA |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
28 | C-TT-2213B | _ | HOLD | HOLD | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
29 | C-TT-2214B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
30 | C-TT-2215B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
31 | C-TT-2216B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
32 | C-TT-2218B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
33 | C-TT-2217B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
34 | C-TT-2219B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
35 | C-TT-2220B | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
36 | TE-2222B TE-2223B TE-2224B | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
37 | TE-2225B TE-2226B TE-2227B | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
38 | TE-2228B TE-2229B TE-2230B | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
39 | TT-2122C | 8" | 250 | 290 | 36.8 | 180 |  | 9 |  | 0-100 | 4.9 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | GAS-111-0031A-AN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
40 | C-TT-2191C | _ | HOLD | HOLD | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Thermowell Nace
41 | TT-2123C | 6" | 250 | 290 | 129 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
42 | TT-2197C | 6" | 200 | 240 | 59.9 | 180 |  | 8 |  | 0-120 | 17.1 / 24.5 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
43 | TT-2123C | 6" | 200 | 240 | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | REMOTE TYPE |  | GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 |  | Loose Item U Size & rating to be chected by client Thermowell Nace
44 | C-TT-2194C | _ | HOLD | HOLD | 148 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
45 | C-TT-2204C | 2" TO 4" (Expanded) | 150 | 200 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
46 | C-TT-2203C | _ | 200 | 250 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
47 | C-TT-2213C | _ | HOLD | HOLD | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
48 | C-TT-2214C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
49 | C-TT-2215C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-120 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
50 | C-TT-2216C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
51 | C-TT-2218C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
52 | C-TT-2217C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
53 | C-TT-2219C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
54 | C-TT-2220C | _ | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
55 | TE-2222C TE-2223C TE-2224C | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
56 | TE-2225C TE-2226C TE-2227C | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
57 | TE-2228C TE-2229C TE-2230C | _ | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7

## DPT
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 10 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V02
Data Sheet for Differential Pressure Transmitter
| 1 | Tag No.: (Refer to Next Page) | Service: (Refer to Next Page)
GENERAL | 2 | Function | Recordo Indicaten Controlo Blindo Transn Intego (Note1)
| 3 | Case | MFR STDn Nom Sizeo Color MFR STDn Other
| 4 | Mounting | Flusho Surfaceo Yoken Other
| 5 | Enclosure Class | General Purposeo Weather Proof n Explosion-Proof o Class
|  |  | For use in Intrinsically Safe Systemn |  |  |  | Other EExia, IIB, T4
| 6 |  | Ingress Protection : IP 66
| 7 | Power Supply | 117 V 60 Hzo Other: aco dcn Volts : 24 VDC Loop Powered
TRANSMITTER | 8 | Trans. Output | 4-20mAn 10-50mAo 21-10 kpa(3-15 psig)o Other 4-20mA Smart HART
| 9 |  | Transmitter Accuracy : Better than 0.1% of Calibrated Span
UNIT | 10 | Service | Flow o Level o Diff. Pressure n Other
| 11 | Element Type | Diaphragmn Helixo Bourdon o Bellowso Other
| 12 | Material | Body Epoxy Painted Die Cast Aluminum Copper free Element 316 S.S. as minimum
| 13 | Range | Fixedo Adj. Range n Set At (Refer to Next Page)
| 14 | Rating | Overrange Protection: at least 1.5 times the maximum range
| 15 | Process Data | Press: Normal Max Element Range (Refer to Next Page)
| 16 | Process Conn. | ½ in. NPTn Other Male with wrench flats
| 17 |  | Location: Bottom n Back o Other
| 18 | Electrical Conn. | MFR STDo Other ISO M20x1.5
OPTIONS | 19 | Miscellaneous | Filt Reg.o Sup. Gageo Output Gageo Charts
| 20 | Diaphragm Seal | Diaph Seal o (N/A) Type : Capillary Length: Mtl. :
Conn. Fill Fluid :
Flushing Connection :
| 21 | Manifold | Valve Manifold : See List
| 22 | MFR. & Model No. | See list
Notes:
1- All transmitters shall be provided complete with LCD type integral indicator .
2- Repeatability of the transmitter shall be better than 0.1% of the span.
3- All transmitters shall be reverse polarity protected.
4- All components, particularly if containing electric contacts, shall be vibration resistant.
5- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## DPT List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 11 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V02
List of DPT
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | DIFFERENTIAL PRESSURE Norm/Max | CALIBRATED RANGE (Barg) | ACCESSORIES | MFR. & Model No. | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Norm. / Design | VISCOSITY (Cst) |  | ACCESSORIES | ACCESSORIES | REV. Remark
1 | PDT-2122A | Process gas Comp A | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
1 | PDT-2132A | Process gas Comp A | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
2 | C-PDT-2204A | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316
3 | PDT-2122B | Process gas Comp A | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
1 | PDT-2132B | Process gas Comp B | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
4 | C-PDT-2204B | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316
5 | PDT-2122C | Process gas Comp A | GAS-111-0031A-AN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 4.9 / 24.5 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
1 | PDT-2132C | Process gas Comp C | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1 | 1/2" NPT | Gas | 17.1 / 24.5 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | NACE material 5 valve manifold S.S316 |  | Loose Item
6 | C-PDT-2204C | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3 | 1/2" NPT | Liquid | 6 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316
7
8
9
10
11

## DPG
NISOC | [9 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 | [9 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [22 empty] | شماره صفحه: 12 از 42
[10 empty] | پروژه |  |  |  |  | بسته کاری |  |  | صادرکننده |  | تسهیلات |  |  | رشته |  |  | نوع مدرک |  |  | سریال |  |  | نسخه
[10 empty] | BK |  |  |  |  | GCS |  |  | HY |  | 120 |  |  | IN |  |  | DS |  |  | 0001 |  |  | V02
Data Sheet for Differential Pressure Gauge
1 | Type : | Direct Rdg. | [5 empty] | 3-15 lb Reciever | [11 empty] | 11 | MFR.& Model No. |  |  |  | SANGAN PG-13-700
|  | Other | liquid filled | [16 empty] | 12 | Press Element : Diaphragm | [9 empty] | Bellows
2 | Mounting : | Direct |  |  | Local | [6 empty] | Yoke |  |  |  | Other | [10 empty] | Other | (Note6)
3 | Dial : | Diameter |  | 160 mm |  |  | Color : White / Black Lettering ,Aluminum Non Rusting Metal | [12 empty] | 13 | Element Mtl. : | [5 empty] | Bronze |  |  | Steel
4 | Case : | SS316 |  |  |  |  | Cast Aluminum | [5 empty] | Phenol | [10 empty] | SS |  |  | Other | 316SS
|  | Other | [17 empty] | 14 | Socket Mtl. : | [5 empty] | Bronze |  |  | Steel
5 | Ring : | Screwed |  |  | Hinged |  |  |  |  | Slip | [13 empty] | SS |  |  | Other | 316SS
|  | Std |  |  | Other | [14 empty] | 15 | Connection-NPT : | [5 empty] | 1/4 in. |  |  | 1/2 in. |  |  |  | Other | NPTM
6 | Blow-out Protection : |  |  |  | None |  |  |  | Back |  |  |  | Disc | [13 empty] | Bottom |  |  | Back
|  | Solid Front | [5 empty] | Other | [11 empty] | 16 | Movement: | [5 empty] | Bronze |  |  | SS
7 | Lens : | Glass |  |  | Plastic |  |  | Safety Glass ( shatter proof) | [16 empty] | Naylon |  |  |  | Other |  |  |  | Stainless Steel
8 | Options : | [18 empty] | 17 | Diaphragm Seal |  |  |  | N/A
[5 empty] | Pulsation Dampener | [5 empty] | Refer to note | [11 empty] | MFR. | [8 empty] | Type
[23 empty] | Wetted Part Mtl. | [8 empty] | Other Mtl.
Fill Fluid :
9 | Nominal Accuracy Required : |  |  |  |  | ±1.6% of full scale | [16 empty] | Process Conn. :
10 | Over range protection : |  |  | 1.3 times the maximum scale reading | [15 empty] | 18 | Ingress Protection : | [5 empty] | IP 65
Item | Tag No. |  | Range (barg) |  |  |  | Process Fluid/State | Design | [5 empty] | Operating |  |  |  |  | Differential Pressure |  |  | LINE NO./EQUIPMENTNO. | [6 empty] | P&ID NO. | [6 empty] | Accessories | MFR.& Model | NOTE
[8 empty] | Press (barg) |  |  | Temp (C°) |  |  | Press (barg) |  |  | Temp (C°) |  | Norm. (bar) | Max. (bar)
1 | C-PDG-2204A |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3 | [6 empty] | 5 valve manifold S.S316
2 | C-PDG-2200A |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 | [6 empty] | 5 valve manifold S.S316
3 | C-PDG-2205A |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0018A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
4 | C-PDG-2206A |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0017A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
5 | C-PDG-2204B |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3 | [6 empty] | 5 valve manifold S.S316
6 | C-PDG-2200B |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 | [6 empty] | 5 valve manifold S.S316
7 | C-PDG-2205B |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0018A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
8 | C-PDG-2206B |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0017A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
9 | C-PDG-2204C |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3 | [6 empty] | 5 valve manifold S.S316
10 | C-PDG-2200C |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 | [6 empty] | 5 valve manifold S.S316
11 | C-PDG-2205C |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0018A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
12 | C-PDG-2206C |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0017A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6 | [6 empty] | 5 valve manifold S.S316
NOTES :

## PSV (hidden)
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 12 Of 66
1 | ITEM |  |  |  | 1 |  |  |  | 2
2 | TAG NO. |  |  |  | 1601CC001A-PSV-5004A |  |  |  | 1601CC001A-PSV-5005A
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 13 Of 66
1 | ITEM |  |  |  | 3 |  |  |  | 4
2 | TAG NO. |  |  |  | 1601CC001B-PSV-5004B |  |  |  | 1601CC001B-PSV-5005B
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/H | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 14 Of 66
1 | ITEM |  |  |  | 5 |  |  |  | 6
2 | TAG NO. |  |  |  | 1602CC001A-PSV-5004A |  |  |  | 1602CC001A-PSV-5005A
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 15 Of 66
1 | ITEM |  |  |  | 7 |  |  |  | 8
2 | TAG NO. |  |  |  | 1602CC001B-PSV-5004B |  |  |  | 1602CC001B-PSV-5005B
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 16 Of 66
1 | ITEM |  |  |  | 9 |  |  |  | 10
2 | TAG NO. |  |  |  | 1601CC001A-RV-5002A |  |  |  | 1601CC001A-PRV-5003A
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 1"-LBO-160CC001-10004-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | ATM |  | ATM | ATM
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 17 Of 66
1 | ITEM |  |  |  | 11 |  |  |  | 12
2 | TAG NO. |  |  |  | 1601CC001B-RV-5002B |  |  |  | 1601CC001B-PRV-5003B
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 18 Of 66
1 | ITEM |  |  |  | 13 |  |  |  | 14
2 | TAG NO. |  |  |  | 1602CC001A-RV-5002A |  |  |  | 1602CC001A-PRV-5003A
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 19 Of 66
1 | ITEM |  |  |  | 15 |  |  |  | 16
2 | TAG NO. |  |  |  | 1602CC001B-RV-5002B |  |  |  | 1602CC001B-PRV-5003B
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.

## TCV (hidden)
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 32 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001A-TCV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 33 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001B-TCV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 34 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001A-TCV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 35 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001B-TCV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## PRV (hidden)
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 36 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001A-PRV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 37 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001B-PRV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 38 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001A-PRV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 38 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001B-PRV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## FG(A)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 13 از 42
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200A | [5 empty] | C-FI-2201A |  | C-FI-2202A |  |  |  | C-FI-2203A
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4 | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 |  | BK-GCS-HY-120-PR-PI-0001-Page4 |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2.2 |  |  | 12.5 |  |  | 1 | 12.5 | 1 |  | 12.5 |  | 2.2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## FG (B)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 14 از 42
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200B | [5 empty] | C-FI-2201B |  | C-FI-2202B |  |  |  | C-FI-2203B
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4 | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 |  | BK-GCS-HY-120-PR-PI-0001-Page4 |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2.2 |  |  | 12.5 |  |  | 1 | 12.5 | 1 |  | 12.5 |  | 2.2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## FG (C)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 15 از 42
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200C | [5 empty] | C-FI-2201C |  | C-FI-2202C |  |  |  | C-FI-2203C
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4 | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4 |  | BK-GCS-HY-120-PR-PI-0001-Page4 |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2.2 |  |  | 12.5 |  |  | 1 | 12.5 | 1 |  | 12.5 |  | 2.2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## SG
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 16 از 42
|  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR SIGHT GLASS
DESIGN DATA
1 | Tag Numbers |  |  |  |  | See Next Page
2 | Pipe Material Class |  |  |  |  | C.S
3 | Service |  |  |  |  | Cooling Water
4 | Operating Pressure |  |  |  |  | See List
5 | Operating Temperature |  |  |  |  | See List
6 | Rating |  |  |  |  | See List
7 | Size Range |  |  |  |  | See List
9 | P&ID Reference |  |  |  |  | See List
SPECIFICATIONS
10 | TYPE |  |  |  |  | Rotary
11 | End Connection |  |  |  |  | Flanged R.F
12 | Cover Type |  |  |  |  | Tempered
13 | Installation Requirements |  |  |  |  | Horizontal or Vertical
MATERIALS
15 | Body |  |  |  |  | C.S
16 | Glass Cover |  |  |  |  | TEMPERED GLASS
17 | Gasket |  |  |  |  | KLINGRIT
18 | Bolts / Studs |  |  |  |  | C.S

## SG List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 17 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
List of Sight Glass
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Oper. / Design
1 | C-SG-2200A | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85
2 | C-SG-2201A | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 2.1/2"#150 | Liquid | 3 / 7 | 65 / 85
3 | C-SG-2202A | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1"#150 | Liquid | 3 / 7 | 65 / 85
4 | C-SG-2203A | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85
5 | C-SG-2200B | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85
6 | C-SG-2201B | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 2.1/2"#150 | Liquid | 3 / 7 | 65 / 85
7 | C-SG-2202B | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1"#150 | Liquid | 3 / 7 | 65 / 85
8 | C-SG-2203B | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85
9 | C-SG-2200C | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85
10 | C-SG-2201C | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 2.1/2"#150 | Liquid | 3 / 7 | 65 / 85
11 | C-SG-2202C | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1"#150 | Liquid | 3 / 7 | 65 / 85
12 | C-SG-2203C | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6 | 1/2"#150 | Liquid | 3 / 7 | 65 / 85

## FT A1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 18 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-AN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 24.5
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 1971 |  | 7918 |  | 8710
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | NA |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2121A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT A2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 19 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2131A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 24.5
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 1971 |  | 7918 |  | 8710
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2197A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT A3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 20 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | m3/h |  |  | 16000
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 976.6 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.4298
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.166 |  |  | 0.0026
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 0.25 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 18.02 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.2
Element | 15 | Tag Number |  |  |  |  | C-FE-2206A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7 / ASTM A194 Gr.2H Galvanized |  |  | ASME B1.1
| 23 | Gasket Type & Material
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~20000m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~200 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 21 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-AN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 24.5
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8668.6
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 5.102 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2121B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 22 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2197B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 62
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8668.6
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2197B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 23 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | m3/h |  |  | 16000
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 976.6 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.4298
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.166 |  |  | 0.0026
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 0.25 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 18.02 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.2
Element | 15 | Tag Number |  |  |  |  | C-FE-2206B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7 / ASTM A194 Gr.2H Galvanized |  |  | ASME B1.1
| 23 | Gasket Type & Material
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~20000m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~200 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 24 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-AN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 24.5
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8668.6
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 5.102 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2121C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 25 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2197C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 62
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8668.6
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.1
Element | 15 | Tag Number |  |  |  |  | FE-2197C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTMB7M/2HM |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8668Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | Nace
| 38 | Wetted Part Material |  |  |  |  | Nace
| 39 | Drains/Vents Material |  |  |  |  | 316SS
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 26 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3"
| 4 | Pipe Material |  | Pipe Insulation
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | m3/h |  |  | 16000
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 976.6 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.4298
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.166 |  |  | 0.0026
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 0.25 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 18.02 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0.2
Element | 15 | Tag Number |  |  |  |  | C-FE-2206C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7 / ASTM A194 Gr.2H Galvanized |  |  | ASME B18.2.1/ASME B18.2.2
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~20000m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~200 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## LG-A
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 27 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213A |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR A
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 65 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | HOLD
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | HOLD
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LG-B
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 28 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213B |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR B
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 65 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | HOLD
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | HOLD
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LG-C
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 29 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213C |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR C
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 65 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | HOLD
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | HOLD
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LTA1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 30 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service |  | Pipe / Equipment No. |  |  | 1601-CC-001A |  |  | TK-2101-WR C
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 65 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | HOLD |  |  | HOLD
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTB1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 31 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | TK-2101-WR B
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 65 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | HOLD |  |  | HOLD
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTC1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 32 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | TK-2101-WR C
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 65 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 2.084
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | HOLD |  |  | HOLD
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## Solenoid Valve
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 33 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
Data Sheet for Solenoid Valve
GENERAL | 1 | TAG NO . |  |  | See List
| 2 | SERVICE |  |  | Instrument Air
| 3 | LINE NO, |  |  | See List |  | _
| 4 | QUNTITY |  |  | See List |  | 1
VALVE BODY | 5 | TYPE |  |  | For single acting
| 6 | SIZE- BODY /PORT |  |  | See List
| 7 | RATING & TYPE CONN. |  |  | NPTF
| 8 | MATERIAL -BODY |  |  | Brass
| 9 | MATERIAL -SEAT |  |  | MFR STD
| 10 | MATERIAL -DIAPHRAGM |  |  | N/A
| 11 | OPERATION DIRECT / PILOT |  |  | Pilot operated |  | DIRECT
| 12 | MANUAL RESET |  |  | N/A |  | _
| 13 | MANUAL OPERATOR |  |  | N/A |  | _
| 14 | PAINTING |  |  | N/A
WHEN DEENERGIZED | 15 | 2 WAY VALVE : OPEN/CLOSE |  |  | YES
| 16 | 3 WAY |  |  | N/A
| 17 | VENT PORT : OPEN/CLOSE |  |  | N/A |  | _
| 18 | PRESS PORT : OPEN/CLOSE |  |  | OPEN |  | _
| 19 | EXTERNAL OVERRIDE |  |  | No |  | _
SOLENOID | 20 | ENCLOSURE |  |  | IP 66
| 21 | VOLTAGE/POWER |  |  | 24 VDC /11W
| 22 | STYLE OF COIL |  |  | MFR STD |  | ENCAPSULATED
| 23 | SINGLE OR DOUBLE COIL |  |  | SINGLE |  | SINGLE
| 24 | INSULATION CLASS |  |  | F |  | F
| 25 | ENCLOSURE MATERIAL |  |  | ALUMINUM |  | F
| 26 | CERTIFICATION |  |  | Eex 'd'-IIB-T4 |  | F
| 27 | ELEC. ENTRY |  |  | M20x1.5 ISO |  | M20 ISO
SERVICE CONDITIONS | 28 | FLUID |  |  | Instrument Air
| 29 | OPER.DIFF.MIN (BAR) |  |  | See List
| 30 | OPER.DIFF.MAX (BAR) |  |  | See List |  | 1"
| 31 | TEMP. NORMAL /MAX |  |  | See List |  | 1"
| 32 | SP.GR |  |  | 1.0
| 33 | VISCOSITY |  |  | N/A |  | 4.5/0.928/0.38
| 34 | VALVE CV |  |  | V.T.A |  | 4.5/0.928/0.38
| 35 | MANUFACTURER |  |  | V.T.A
| 36 | MODEL NO. |  |  | V.T.A
37
NOTE: VTA:Vendor To Advise N/A:Not Applicable

## List of SOV
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 34 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
List of SOV
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. |  |  | OPERATING/DESIGNPRESSSURE (Barg) | TEMPERATURE (C) | SOLENOID VALVE SIZE | REMARKS
[7 empty] | Min. / Des. | Norm. / Design
1 | C-SV-2201A | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 6 / 12.5 | 65 / 85 | 1/2"
2 | C-SV-2202A | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 6 / 12.5 | 65 / 85 | 1/2"
3 | C-SV-2203A | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 7 / 12.5 | 65 / 85 | 1/2"
4 | C-SV-2201B | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 8 / 12.5 | 65 / 85 | 1/2"
5 | C-SV-2202B | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 9 / 12.5 | 65 / 85 | 1/2"
6 | C-SV-2203B | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 10 / 12.5 | 65 / 85 | 1/2"
7 | C-SV-2201C | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 11 / 12.5 | 65 / 85 | 1/2"
8 | C-SV-2202C | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 12 / 12.5 | 65 / 85 | 1/2"
9 | C-SV-2203C | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2 |  |  | 6 / 12.5 | 65 / 85 | 1/2"

## VT & ZE A
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 35 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
SERVICE | Tag Number | C-VE-2200A C-VE-2201A C-VE-2202A |  |  |  |  | C-ZE-2200A C-ZE-2201A
| Service | Frame vibration |  |  |  |  | Cylinder Rod Drop Detector
| P&ID No. | BK-GCS-HY-120-PR-PI-0001-Page7 |  |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
| Q'TY | 3 |  |  |  |  | 2
OPERATING CONDITION | Press. Nor(Kg/㎠g) | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Temp. Nor(℃) | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃
Humidity
| Explosion Class & Cert. | Ex ia IIC, T4 | Ex ia IIC, T4 |  |  | Ex ia IIC, T4 | Ex ia IIB, T4 |  |  | Ex ia IIC, T4 | Ex ia IIC, T4 | Ex ia IIC, T4
GENERAL | Description | Frame vibration | Frame vibration |  |  | Frame vibration | Cylinder Rod Drop Detector |  |  | Frame vibration | Frame vibration | Frame vibration
| Manufacturer | Metrix | Metrix |  |  | Metrix | SHINKAWA |  |  | Metrix | Metrix | Metrix
| Model No. - Probe | [5 empty] | FL-452F11L-M9-00-09-10/E50/Z05
| - Ext. Cable | N/A | N/A |  |  | N/A | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50
| - Proximitor | N/A | N/A |  |  | N/A | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50
| Piston Rod Material | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
PROBE | Type | Seismic Vibration | Seismic Vibration |  |  | Seismic Vibration | Proximity |  |  | Seismic Vibration | Seismic Vibration | Seismic Vibration
| Range | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS |  |  | 25.4mm/SEC, RMS | 4.0 mm |  |  | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS
| Material | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel
| Conduit size | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Probe Cable Length | N/A | N/A |  |  | N/A | 1.0 Meter + Ext 9 Meter |  |  | N/A | N/A | N/A
| Sealing | IP66 | IP66 |  |  | IP66 | IP66 |  |  | IP66 | IP66 | IP66
| Sensor Mounting | M8 x P1.25 | M8 x P1.25 |  |  | M8 x P1.25 | Internal of Bare block |  |  | M8 x P1.25 | M8 x P1.25 | M8 x P1.25
| Mounting Housing | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Mounting Thread | N/A | N/A |  |  | N/A | M16x1.5 |  |  | N/A | N/A | N/A
| Sensitivity | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g | 100 mV/g
| Standard | API 670 | API 670 |  |  | API 670 | API 670 |  |  | API 670 | API 670 | API 670
TRANSMITTER | Input Power | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) | 24 VDC(Loop Powered)
| Output | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA | 4~20 mA
| Enclosure Class | IP66 | IP66 |  |  | IP66 | Without |  |  | IP66 | IP66 | IP66
| Model No. | VST5484E | VST5484E |  |  | VST5484E | VM-21T1-22C012-1 |  |  | VST5484E | VST5484E | VST5484E
Notes :

## VT & ZE B
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 36 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
SERVICE | Tag Number | C-VE-2200B C-VE-2201B C-VE-2202B |  |  |  |  | C-ZE-2200B C-ZE-2201B
| Service | Frame vibration |  |  |  |  | Cylinder Rod Drop Detector
| P&ID No. | BK-GCS-HY-120-PR-PI-0001-Page7 |  |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
| Q'TY | 3 |  |  |  |  | 2
OPERATING CONDITION | Press. Nor(Kg/㎠g) | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Temp. Nor(℃) | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃
Humidity
| Explosion Class & Cert. | Ex ia IIC, T4 | Ex ia IIC, T4 |  |  | Ex ia IIC, T4 | Ex ia IIB, T4 |  |  | Ex ia IIC, T4 | Ex ia IIC, T4 | Ex ia IIC, T4
GENERAL | Description | Frame vibration | Frame vibration |  |  | Frame vibration | Cylinder Rod Drop Detector |  |  | Frame vibration | Frame vibration | Frame vibration
| Manufacturer | Metrix | Metrix |  |  | Metrix | SHINKAWA |  |  | Metrix | Metrix | Metrix
| Model No. - Probe | [5 empty] | FL-452F11L-M9-00-09-10/E50/Z05
| - Ext. Cable | N/A | N/A |  |  | N/A | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50
| - Proximitor | N/A | N/A |  |  | N/A | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50
| Piston Rod Material | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
PROBE | Type | Seismic Vibration | Seismic Vibration |  |  | Seismic Vibration | Proximity |  |  | Seismic Vibration | Seismic Vibration | Seismic Vibration
| Range | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS |  |  | 25.4mm/SEC, RMS | 4.0 mm |  |  | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS
| Material | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel
| Conduit size | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Probe Cable Length | N/A | N/A |  |  | N/A | 1.0 Meter + Ext 9 Meter |  |  | N/A | N/A | N/A
| Sealing | IP66 | IP66 |  |  | IP66 | IP66 |  |  | IP66 | IP66 | IP66
| Sensor Mounting | M8 x P1.25 | M8 x P1.25 |  |  | M8 x P1.25 | Internal of Bare block |  |  | M8 x P1.25 | M8 x P1.25 | M8 x P1.25
| Mounting Housing | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Mounting Thread | N/A | N/A |  |  | N/A | M16x1.5 |  |  | N/A | N/A | N/A
| Sensitivity | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g | 100 mV/g
| Standard | API 670 | API 670 |  |  | API 670 | API 670 |  |  | API 670 | API 670 | API 670
TRANSMITTER | Input Power | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) | 24 VDC(Loop Powered)
| Output | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA | 4~20 mA
| Enclosure Class | IP66 | IP66 |  |  | IP66 | Without |  |  | IP66 | IP66 | IP66
| Model No. | VST5484E | VST5484E |  |  | VST5484E | VM-21T1-22C012-1 |  |  | VST5484E | VST5484E | VST5484E
Notes :

## VT & ZE C
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 37 از 42
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
SERVICE | Tag Number | C-VE-2200C C-VE-2201C C-VE-2202C |  |  |  |  | C-ZE-2200C C-ZE-2201C
| Service | Frame vibration |  |  |  |  | Cylinder Rod Drop Detector
| P&ID No. | BK-GCS-HY-120-PR-PI-0001-Page7 |  |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
| Q'TY | 3 |  |  |  |  | 2
OPERATING CONDITION | Press. Nor(Kg/㎠g) | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Temp. Nor(℃) | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ |  |  | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃ | ₋ 40℃ to +100℃
Humidity
| Explosion Class & Cert. | Ex ia IIC, T4 | Ex ia IIC, T4 |  |  | Ex ia IIC, T4 | Ex ia IIB, T4 |  |  | Ex ia IIC, T4 | Ex ia IIC, T4 | Ex ia IIC, T4
GENERAL | Description | Frame vibration | Frame vibration |  |  | Frame vibration | Cylinder Rod Drop Detector |  |  | Frame vibration | Frame vibration | Frame vibration
| Manufacturer | Metrix | Metrix |  |  | Metrix | SHINKAWA |  |  | Metrix | Metrix | Metrix
| Model No. - Probe | [5 empty] | FL-452F11L-M9-00-09-10/E50/Z05
| - Ext. Cable | N/A | N/A |  |  | N/A | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50 | FW-452FT-80/E50
| - Proximitor | N/A | N/A |  |  | N/A | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50 | FK-452F2-1-2/E50
| Piston Rod Material | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
PROBE | Type | Seismic Vibration | Seismic Vibration |  |  | Seismic Vibration | Proximity |  |  | Seismic Vibration | Seismic Vibration | Seismic Vibration
| Range | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS |  |  | 25.4mm/SEC, RMS | 4.0 mm |  |  | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS | 25.4mm/SEC, RMS
| Material | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel |  |  | 316 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel
| Conduit size | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Probe Cable Length | N/A | N/A |  |  | N/A | 1.0 Meter + Ext 9 Meter |  |  | N/A | N/A | N/A
| Sealing | IP66 | IP66 |  |  | IP66 | IP66 |  |  | IP66 | IP66 | IP66
| Sensor Mounting | M8 x P1.25 | M8 x P1.25 |  |  | M8 x P1.25 | Internal of Bare block |  |  | M8 x P1.25 | M8 x P1.25 | M8 x P1.25
| Mounting Housing | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A
| Mounting Thread | N/A | N/A |  |  | N/A | M16x1.5 |  |  | N/A | N/A | N/A
| Sensitivity | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g |  |  | 100 mV/g | 100 mV/g | 100 mV/g
| Standard | API 670 | API 670 |  |  | API 670 | API 670 |  |  | API 670 | API 670 | API 670
TRANSMITTER | Input Power | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) |  |  | 24 VDC(Loop Powered) | 24 VDC(Loop Powered) | 24 VDC(Loop Powered)
| Output | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA |  |  | 4~20 mA | 4~20 mA | 4~20 mA
| Enclosure Class | IP66 | IP66 |  |  | IP66 | Without |  |  | IP66 | IP66 | IP66
| Model No. | VST5484E | VST5484E |  |  | VST5484E | VM-21T1-22C012-1 |  |  | VST5484E | VST5484E | VST5484E
Notes :

## LTA2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 38 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 300mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTB2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 39 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 300mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
Miscell | 46 | Manufacturer
| 47 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTC2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 40 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 300mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 250barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
Miscell | 46 | Manufacturer
| 47 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## PS
NISOC |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 41 از 42
|  |  |  | پروژه |  | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
|  |  |  | BK |  | GCS | HY | 120 | IN | DS |  | 0001 |  | V02
Instrument Data Sheet For Pressure Switch
GENERAL | [9 empty] | SWITCH
1 | Press. |  |  |  | Vaccum |  |  |  |  | 8 | Type: |  | Mercury |  |  |  | Snap
| Comp. |  |  |  | Diff. Press. | [7 empty] | Other :
2 |  | Set In Field |  |  |  | Factory Set |  |  |  | 9 | Quantity: |  | Single |  |  |  | Dual
|  | Internal |  |  | External |  |  | Dial |  | 10 | Form: |  | SPST |  |  | SPDT |  |  | DPDT
3 |  | Fixed |  |  | Adj. |  |  | Min. |  |  |  |  | Other:
ELEMENT | [9 empty] | 11 | Max Rating: |  | 10 Amps |  |  | 24vdc
4 | Diaphragm |  |  |  | Bourdon |  |  | Bellows |  |  |  |  | Other:
[10 empty] | 12 | Load: |  | Inductive |  |  |  | Non-Inductive
5 | Material |  |  |  | Aluminum |  |  |  |  | 13 | IP |  | IP66 Exd/IIB T4 |  |  |  |  | SIL Certified
6 | Connection | 1/2"NPT |  |  |  | Other Size : |  |  |  | 14 | Electrical Connection: |  |  |  | M20x1.5
|  | Bottom |  |  |  | Back |  |  |  | 15 | Manufacturer & Model No.
7 |  | Local |  |  | Surface |  |  | Flush |  | 16 | Accessories |  | Manifold 2Valve
Tag No. |  |  | Process Connection |  |  | Adj. Range |  |  | Set Point |  | Pressure |  | Service or Line Number | [5 empty] | Remark
[6 empty] | (Bar G) |  |  | (Bar G) |  | Design | Working
PS-2133A |  |  | 1 " NPT |  |  | 0~80 |  |  | HOLD |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204A |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220A |  |  | 1 " NPT |  |  | 0~10 |  |  | 1 |  | 10Bar | 3 Bar | CWS-112-0002A-C.S-3"-IS
PS-2133B |  |  | 1 " NPT |  |  | 0~80 |  |  | HOLD |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204B |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220B |  |  | 1 " NPT |  |  | 0~10 |  |  | 1 |  | 10Bar | 3Bar | CWS-112-0002A-C.S-3"-IS
PS-2133C |  |  | 1 " NPT |  |  | 0~80 |  |  | HOLD |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204C |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220C |  |  | 1 " NPT |  |  | 0~10 |  |  | 1 |  | 10Bar | 3Bar | CWS-112-0002A-C.S-3"-IS

## TS
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 42 از 42
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V02
Instrument Data Sheet For Temperature Switch
GENERAL
1.TAG.NO |  | C-TS-2191A |  | C-TS-2194A |  | C-TS-2191B |  |  | C-TS-2194B |  | C-TS-2191C | C-TS-2194C
2.Equipment |  | 1ST STAGE DISCHARGE SNUBBER |  | 2ND STAGE DISCHARGE SNUBBER |  | 1ST STAGE DISCHARGE SNUBBER |  |  | 2ND STAGE DISCHARGE SNUBBER |  | 1ST STAGE DISCHARGE SNUBBER | 2ND STAGE DISCHARGE SNUBBER
3.ENCLOSURE MATERIAL |  | Cast Aluminum |  | Cast Aluminum |  | Cast Aluminum |  |  | Cast Aluminum |  | Cast Aluminum | Cast Aluminum
4.SERVICE |  | Gas |  | Gas |  | Gas |  |  | Gas |  | Gas | Gas
5.RANGE |  | 0-200C |  | 0-200'C |  | 0-200'C |  |  | 0-200'C |  | 0-200'C | 0-200'C
6.Ingress Protection |  | IP 66/Exd-IIB-T4 SIL Certified
THERMOWELL
7.TYPE SYSTEM |  | Flnage |  | Flange |  | Flange |  |  | Flange |  | Flange | Flange
8 MATERIAL |  | AISI 316/Nace |  | AISI 316/Nace |  | AISI 316/Nace |  |  | AISI 316/Nace |  | AISI 316/Nace | AISI 316/Nace
9.CONNECTION LOCATION |  | Bottom |  | Bottom |  | Bottom |  |  | Bottom |  | Bottom | Bottom
10.TUBING LENGTH |  | N/A |  | N/A |  | N/A |  |  | N/A |  | N/A | N/A
11.TUBING TYPE & MATERIAL |  | N/A |  | N/A |  | N/A |  |  | N/A |  | N/A | N/A
12.WELL CONN.SIZE & TYPE |  | 2"#300 |  | 2"#600 |  | 2"#300 |  |  | 2"#600 |  | 2"#300 | 2"#600
13.WELL MATERIAL |  | 316 S.S |  | 316 S.S |  | 316 S.S |  |  | 316 S.S |  | 316 S.S | 316 S.S
14.'U' DIMENSION(NOMINAL) |  | 400mm |  | 400mm |  | 400mm |  |  | 400mm |  | 400mm | 400mm
SWITCH
15.TYPE |  | Snap Action |  | Snap Action |  | Snap Action |  |  | Snap Action |  | Snap Action | Snap Action
16.QUANTITY | FORM | 1/DPDT |  | 1/DPDT |  | 1/DPDT |  |  | 1/DPDT |  | 1/DPDT | 1/DPDT
17.ENCLOSURE |  | IP66 |  | IP66 |  | IP66 |  |  | IP66 |  | IP66 | IP66
18.RATING:VOLTS |  | 24 VDC |  | 24 VDC |  | 24 VDC |  |  | 24 VDC |  | 24 VDC | 24 VDC
19.AMPS |  | 2 |  | 2 |  | 2 |  |  | 2 |  | 2 | 5
20.LOAD TYPE |  | INDUCTIVE |  | INDUCTIVE |  | INDUCTIVE |  |  | INDUCTIVE |  | INDUCTIVE | INDUCTIVE
21.DIFF.:FIXED | ADJUST | YES/- |  | YES/- |  | YES/- |  |  | YES/- |  | YES/- | YES/-
22.ELECTRICAL CONNECTION |  | M20*1.5 |  | M20*1.5 |  | M20*1.5 |  |  | M20*1.5 |  | M20*1.5 | M20*1.5
23.Accuracy |  | 1% Of Spna |  | 1% Of Spna |  | 1% Of Spna |  |  | 1% Of Spna |  | 1% Of Spna | 1% Of Spna
SERVICE CONDITIONS
27.TEMP.:OPER 'C |  | 129'C |  | 148'C |  | 129'C |  |  | 148'C |  | 129'C | 148'C
28.PRESS.:OPER 'C |  | 18 |  | 54.9 |  | 18 |  |  | 54.9 |  | 18 | 54.9
29.TRIP POINT 'C |  | 159 |  | 178 |  | 159 |  |  | 178 |  | 159 | 178
30.MANUFACTURER |  | HOLD |  | Hold |  | Hold |  |  | Hold |  | Hold | Hold
31.MANUFACTURER'S MODEL NO. |  | HOLD |  | HOLD |  | HOLD |  |  | HOLD |  | HOLD | HOLD