## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-DW-0003_V00 |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-SVTR-HY-0027 |  |  | Transmital Date:18 sep 2023
Document Title: JB TERMINATION DRAWING
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-IN-DW-0003_V00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) و سازنده مي باشد. |  | BK-SUR-ENG-MEC-02-08564 | 2023-10-07
2 | ضخامت JB سه میلیمتر در نظر گرفته شود. |  | BK-SUR-ENG-MEC-02-08564 | 2023-10-07
3 | فرمت مدرک فوق قابل قبول نمی باشد و می بایست مطابق روال مهندسی ارایه گردد. در خصوص screen/Overall Screen بصورت شماتیک نمایش داده شود. |  | BK-SUR-ENG-MEC-02-08564 | 2023-10-07
4 | بر اساس spec پروزه Protection class of cable glands shall be Eexd می باشد. |  | BK-SUR-ENG-MEC-02-08564 | 2023-10-07
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: s.akbari | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 10/7/2023 |  |  |  |  | Date: