## Sheet2
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 27
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 0005 | V01
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST نگهداشت و افزایش تولید میدان نفتی بینک
V01 |  | Jan.2024 |  | IFR |  |  |  | HAVAYAR |  |  | M.Fakharian |  | S.Faramarzpour
V00 |  | MAY.2023 |  | IFR |  |  |  | HAVAYAR |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Sheet1
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از27
9184 – 073 - 053 |  |  | BK | GCS |  | HY | 120 | IN | LI | 0005 |  | V01
REVISION RECORD SHEET
Page | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 |  | X | [6 empty] | 74
11 |  | X | [6 empty] | 75
12 |  | X | [6 empty] | 76
13 |  | X | [6 empty] | 77
14 |  | X | [6 empty] | 78
15 |  | X | [6 empty] | 79
16 |  | X | [6 empty] | 80
17 |  | X | [6 empty] | 81
18 |  | X | [6 empty] | 82
19 |  | X | [6 empty] | 83
20 |  | X | [6 empty] | 84
21 |  | X | [6 empty] | 85
22 |  | X | [6 empty] | 86
23 |  | X | [6 empty] | 87
24 |  | X | [6 empty] | 88
25 |  | X | [6 empty] | 89
26 |  | X | [6 empty] | 90
27 |  | X | [6 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## LEGEND
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 37
9184 – 073 - 053 |  |  |  | BK | GCS | HY | 120 | IN | LI | 0005 | V01
ABBREVIATIONS
| Location: |  | (Geographical location of the instrument) | [6 empty] | Valve Action :
| FIELD | : | Local | [6 empty] | FC | : | Fail Close
| LCP | : | Local Panel | [6 empty] | FO | : | Fail Open
| SS | : | Electrical Substation | [6 empty] | FL | : | Fail Lock
| ITR | : | Instrument Technical Room | [6 empty] | FLC | : | Fail Lock Close
| CCR | : | Central Control Room | [6 empty] | FLO | : | Fail Lock Open
| MCC | : | Motor Control Center
| DCS | : | Distributed Control System
| ESD | : | Emergency Shutdown System | [6 empty] | W/D :
| UCP | : | Unit Control Panel | [6 empty] | D | : | Dry Contact
[10 empty] | W | : | Wet Contact
| I/O type | [8 empty] | Power Supply :
| AI | : | Analog Input | [6 empty] | AC110V
| AO | : | Analog Output | [6 empty] | DC24V
| DI | : | Digital Input
| DO | : | Digital Output
| DOR | : | Digital Output redundant
| AIR | : | Analog Input redundant
| AIRF | : | Analog Input redundant FAII SAFE
| AOR | : | Analog Output redundant
| DIR | : | Digital Input redundant
| DIRF | : | Digital Input redundant FAIL SAFE
| SAI | : | Software Analog Input
| SAO | : | Software Analog Output
| SDI | : | Software Digital Input
| SDO | : | Software Digital Output
| F |  | fail safe
System:
| ESD | : | Emergency Shut Down System
| UCP | : | Unit Control Panel
| DCS | : | Distributed Control System (PCS)
| FGS | : | Fire and Gas System
| MCC | : | Motor Control Center
Signal Type :
4-20mA
DC24V
| NC |  | Contact (Normal Close)
| NO |  | Contact (Normal Open)
| SOV |  | Digital Output Solenoid Valve
| SL |  | Serial Link
Refrence Doc:
BK-GCS-HY-120-PR-PI-0001 P&I DIAGRAM

## LIST-A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 27 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201A | POSV-2201A | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-2101A | JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
2 | POSV-2202A | POSV-2202A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-2101A | JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
3 | POSV-2203A | POSV-2203A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-2101A | JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
4 | POSV-2204A | POSV-2204A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-2101A | JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
5 | POSV-2205A | POSV-2205A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DOR | UCP-2101A | JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
6 | POSV-2123A | POSV-2123A | A | SOLENOID VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET1A |  |  |  | DOR | UCP-2101A | JBU-S-2101 | 24VDC | W |  | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
7 | CZSO-2123A | CZSO-2123A | A | LIMIT SWITCH | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET1A |  |  |  | DI | JBU-D-2101 | UCP-2101A | 24VDC | W |  | NIS
| CZSC-2123A | CZSC-2123A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET1A |  |  |  | DI | JBU-D-2101 | UCP-2101A | 24VDC | W |  | NIS
8 | FI-2121A | FT-2121A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
9 | TI-2122A | TT-2122A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
10 | PDI-2122A | PDT-2122A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
11 | PI-2123A | PT-2123A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
12 | TI-2123A | TT-2123A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
13 | PI-2124A | PT-2124A | A | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
14 | FI-2131A | FT-2131A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
15 | TI-2132A | TT-2132A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
16 | PI-2132A | PT-2132A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
17 | PDI-2132A | PDT-2132A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
18 | TI-2133A | TT-2133A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
19 | PI-2133A | PT-2133A | A | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
20 | PCY-2123A | PCY-2123A | A | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AOR | UCP-2101A | JBU-A-2101 |  |  | 4-20mA | IS
|  | PCYZ-2123A |  | Feed back |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | JBU-A-2101 | UCP-2101A |  |  | 4-20mA | IS
|  | PCYZI-2123A |  | Feed back |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS |  |  | 4-20mA | IS
21 | TI-2191A | TT-2191A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
22 | TI-21941A | TT-2194A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | JBU-A-2101A | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | PCS
23 | PI-2201A | PT-2201A | A | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A | 2" |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | Serial link | UCP-2101A | PCS
24 | PI-2210A | PT-2210A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | Serial link | UCP-2101A | PCS
25 | PI-2211A | PT-2211A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | Serial link | UCP-2101A | PCS
26 | PI-2200A | PT-2200A | A | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | HOLD |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
27 | LI-2200A | LT-2200A | A | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-300 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200A |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
28 | TI-2203A | TT-2203A | A | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AIR | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
29 | TI-2214A | TT-2214A | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2214A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
30 | TI-2215A | TT-2215A | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2215A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
31 | TI-2216A | TT-2216A | A | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | JBU-A-2101A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | TI-2216A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
32 | TI-2217A | TT-2217A | A | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | JBU-A-2101A | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | TI-2217A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
33 | TI-2218A | TT-2218A | A | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | JBU-A-2101A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | TI-2218A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
34 | TI-2219A | TT-2219A | A | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | JBU-A-2101A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | TI-2219A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
35 | TI-2220A | TT-2220A | A | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | JBU-A-2101A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | TI-2220A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
36 | FI-2206A | FT-2206A | A | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AI | JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-20000 | m3/h |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | PCS
37 | PI-2204A | PT-2204A | A | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 2" |  |  | AIR | JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
38 | TI-2204A | TT-2204A | A | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 4" |  |  | AI | JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
39 | PDI-2204A | PDT-2204A | A | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 1" |  |  | AI | JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | PCS
-
40 | PI-2220A | PT-2220A | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AIR | JBU-A-2103A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | PCS
41 | PI-2221A | PT-2221A | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AI | JBU-A-2103A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2221A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | PCS
42 | LI-2213A | LT-2213 A | A | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | AIR | JBU-A-2103A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213A |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | PCS
43 | TI-2213A | TT-2213A | A | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | AIR | JBU-A-2103A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | PCS
44 | VI-2200A | VT-2200A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | JBU-A-2104A | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | VI-2200A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
45 | VI-2201A | VT-2201A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | JBU-A-2104A | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | VI-2201A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
45 | VI-2202A | VT-2202A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | JBU-A-2104A | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A
|  | VI-2202A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
46 | ZI-2200A | ZT-2200A | A | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200A |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
47 | ZI-2201A | ZT-2201A | A | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201A |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
48 | XI-2200A | XT-2200A | A | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200A |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
49 | TI-2222A | TE-2222A | A | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A |  |  | 4-20mA
|  | TI-2222A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
50 | TI-2225A | TE-2225A | A | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A |  |  | 4-20mA
|  | TI-2225A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
51 | TI-2228A | TE-2228A | A | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A |  |  | 4-20mA
|  | TI-2228A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | PCS
52 | TI-2191A | TS-2191A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | JBU-D-2101A | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 0-200 | °C
|  | TI-2191A |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | DIRF | Trip Relay UCP A | UCP-2101A | 24VDC
|  | TA-2191A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | PCS | 24VDC
53 | TI-2194A | TS-2194A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 0-200 | °C
|  | TI-2194A |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A
|  | TA-2194A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | PCS | 24VDC
54 | PI-2133A | PS-2133A | A | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | - | JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 0-80 | BARG
|  | PI-2133A |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A
|  | PA-2133A |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | PCS | 24VDC
55 | PI-2204A | PS-2204A | A | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | JBU-D-2101A | Trip Relay UCP A |  |  |  | N'IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204A |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A
|  | PA-2204A |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | Serial link | UCP-2101A | PCS | 24VDC
56 | PI-2220A | PS-2220A | A | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | - | JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 0-10 | BARG
|  | PI-2220A |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A
|  | PA-2220A |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | PCS | 24VDC
57 | XSS-2200A | XSS-2200A | A | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
58 | XSP-2200A | XSP-2200A | A | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
59 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
60 | XR-2200A | XR-2200A | A | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
61 | XF-2200A | XF-2200A | A | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSS-2201A | XSS-2201A | A | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | XSP-2201A | XSP-2201A | A | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
64 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XR-2201A | XR-2201A | A | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XF-2201A | XF-2201A | A | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSS-2202A | XSS-2202A | A | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
68 | XSP-2202A | XSP-2202A | A | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
69 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XR-2202A | XR-2202A | A | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XF-2202A | XF-2202A | A | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2203A | XSP-2203A | A | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
73 | XSS-2203A | XSS-2203A | A | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XR-2203A | XR-2203A | A | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XF-2203A | XF-2203A | A | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | XSS-2205A | XSS-2205A | A | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XSP-2205A | XSP-2205A | A | STOP COMMAND LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
79 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XR-2205A | XR-2205A | A | RUNNING STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XF-2205A | XF-2205A | A | FAILURE STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
82 | XSS-2220A | XSS-2220A | A | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XSP-2220A | XSP-2220A | A | STOP COMMAND WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
84 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XR-2220A | XR-2220A | A | RUNNING STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XF-2220A | XF-2220A | A | FAILURE STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
87 | XSS-2221A | XSS-2221A | A | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XSP-2221A | XSP-2221A | A | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
89 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XR-2221A | XR-2221A | A | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XF-2221A | XF-2221A | A | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
92 | XSS-2222A | XSS-2222A | A | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XSP-2222A | XSP-2222A | A | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
94 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XR-2222A | XR-2222A | A | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XF-2222A | XF-2222A | A | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
97 | XSS-2223A | XSS-2223A | A | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XSP-2223A | XSP-2223A | A | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
99 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XR-2223A | XR-2223A | A | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XF-2223A | XF-2223A | A | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
102 | XSS-2224A | XSS-2224A | A | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XSP-2224A | XSP-2224A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
104 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XR-2224A | XR-2224A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XF-2224A | XF-2224A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
107 | XSS-2225A | XSS-2225A | A | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XSP-2225A | XSP-2225A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
109 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XR-2225A | XR-2225A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XF-2225A | XF-2225A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
112 |  | HST-2230A | A | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 |  | HSP-2230A | A | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 |  | HSL-2230A | A | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 |  | HSR-2230A | A | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 |  | HST-2231A | A | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
117 |  | HSP-2231A | A | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 |  | HSL-2231A | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 |  | HSR-2231A | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 |  | HST-2232A | A | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 |  | HSP-2232A | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
122 |  | HSL-2232A | A | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 |  | HSR-2232A | A | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
124 |  | HST-2233A | A | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2233A | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2233A | A | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2233A | A | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2234A | A | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2234A | A | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2234A | A | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2234A | A | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2235A | A | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2235A | A | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2235A | A | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2235A | A | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2236A | A | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2236A | A | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2236A | A | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2236A | A | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HSL-2237A | A | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HST-2237A | A | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSP-2237A | A | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2237A | A | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2239A | A | PUSH BUTTON | WATER COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2239A | A | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2239A | A | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2239A | A | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2240A | A | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2240A | A | PUSH BUTTON | BARRING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2240A | A | SELECTOR SWITCH | BARRING MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2240A | A | SELECTOR SWITCH | BARRING MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HST-2242A | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HSP-2242A | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSL-2242A | A | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSR-2242A | A | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HST-2243A | A | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSP-2243A | A | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2243A | A | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2243A | A | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HSL-2241A | A | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSR-2241A | A | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSR-2242A | A | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HST-2241A | A | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | ESDL-2230A | A | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DIRF | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSL-2242A1 | A | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HSL-2242A2 | A | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSL-2242A3 | A | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2242A4 | A | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSL-2242A5 | A | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | XR-2230A | A | SIGNAL LAMP | OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | XR-2231A | A | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | XR-2232A | A | SIGNAL LAMP | LUBRICATOR HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | XR-2233A | A | SIGNAL LAMP | LUBRICATOR MOTOR ACTIVE LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | XR-2234A | A | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | XR-2235A | A | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | XR-2236A | A | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | XR-2237A | A | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | XR-2238A | A | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | XR-2239A | A | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | XR-2240A | A | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | XR-2242A | A | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | XR-2243A | A | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101A | AK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | XSP-2230A | A | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XF-2230A | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | ESDL-2230A | A | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 | PSOV-2121A | PSOV-2121A | A | ON OFF VALVE SOLENOID | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DOR | UCP-2101A | JBU-S-2101 | 24VDC | W | 24VDC | NIS | FO | [9 empty] | Valve is in client scope of supply
[6 empty] | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
187 | XZIC-2121A | XZIC-2121A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | JBU-D-2101 | UCP-2101A | 24VDC | W | 24VDC | NIS
188 | XZIO-2121A | XZIO-2121A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | JBU-D-2101 | UCP-2101A | 24VDC | W | 24VDC | NIS
189 | PSOV-2233A | PSOV-2233A | A | ON OFF VALVE SOLENOID | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DOR | UCP-2101A | FIELD | 24VDC | W | 24VDC | NIS | FO
[6 empty] | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
190 | XZIC-2133A | XZIC-2133A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | FIELD | UCP-2101A | 24VDC | W | 24VDC | NIS
191 | XZIO-2133A | XZIO-2133A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1A |  |  |  | DI | FIELD | UCP-2101A | 24VDC | W | 24VDC | NIS
192 |  | ESD-01A | A | ESD |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIRF | ESD | UCP-2101A | 24VDC | W | 24VDC | NIS
193 |  | ESD-02A | A | ESD |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIRF | ESD | UCP-2101A | 24VDC | W | 24VDC | NIS
194 |  | ESD-02 | A | ESD |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIRF | ESD | UCP-2101A | 24VDC | W | 24VDC | NIS
195 |  | USD-05A | A | ESD |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DOR | UCP-2101A | ESD | 24VDC | D | 24VDC | NIS
196 |  | PT-2121A | A | SPILL BACK |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | AIR | FCS | UCP-2101A | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
197 |  | XS-2100A | A | Time Syc |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DI | FCS | UCP-2101A | 24VDC | W | 24VDC | NIS
198 |  | HSS-2125A | A | Permission to start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIR | FCS | UCP-2101A | 24VDC | W | 24VDC | NIS
199 |  | HSS-2123A | A | Command Start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIR | FCS | UCP-2101A | 24VDC | W | 24VDC | NIS
200 |  | HSP-2123A | A | Command Stop |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIR | FCS | UCP-2101A | 24VDC | W | 24VDC | NIS
201 |  | HSS-2124A | A | Ready to Start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DO | UCP-2101A | FCS | 24VDC | D | 24VDC | NIS
202 |  | XR-2121A | A | Running Status |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DO | UCP-2101A | FCS | 24VDC | D | 24VDC | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 29 | 5.8 | 35
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 11 | 2.2 | 14
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 83 | 16.6 | 100
|  |  | 6 | DIR | 3 | 0.6 | 4
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 21 | 4.2 | 26
|  |  | 9 | DOR | 31 | 6.2 | 37
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
Note on B164: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C164: Forouzandeh Fatemeh: ALARM L,H چک شود

## LIST-B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 27 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201B | POSV-2201B | B | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-2101B | JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
2 | POSV-2202B | POSV-2202B | B | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-2101B | JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
3 | POSV-2203B | POSV-2203B | B | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-2101B | JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
4 | POSV-2204B | POSV-2204B | B | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-2101B | JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
5 | POSV-2205B | POSV-2205B | B | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DOR | UCP-2101B | JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
6 | POSV-2123B | POSV-2123B | B | SOLENOID VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET1B |  |  |  | DOR | UCP-2101B | JBU-S-2102 | 24VDC | W |  | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
7 | CZSO-2123B | CZSO-2123B | B | LIMIT SWITCH | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET1B |  |  |  | DI | JBU-D-2102 | UCP-2101B | 24VDC | W |  | NIS
| CZSC-2123B | CZSC-2123B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET1B |  |  |  | DI | JBU-D-2102 | UCP-2101B | 24VDC | W |  | NIS
8 | FI-2121B | FT-2121B | B | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
9 | TI-2122B | TT-2122B | B | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
10 | PDI-2122B | PDT-2122B | B | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
11 | PI-2123B | PT-2123B | B | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
12 | TI-2123B | TT-2123B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
13 | PI-2124B | PT-2124B | B | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
14 | FI-2131B | FT-2131B | B | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
15 | TI-2132B | TT-2132B | B | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
16 | PI-2132B | PT-2132B | B | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
17 | PDI-2132B | PDT-2132B | B | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
18 | TI-2133B | TT-2133B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
19 | PI-2133B | PT-2133B | B | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
20 | PCY-2123B | PCY-2123B | B | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AOR | UCP-2101B | JBU-A-2102 |  |  | 4-20mA | IS
|  | PCYZ-2123B |  | Feed back |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2102 | UCP-2101B |  |  | 4-20mA | IS
|  | PCYZI-2123B |  | Feed back |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS |  |  | 4-20mA | IS
21 | TI-2191B | TT-2191B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
22 | TI-21941B | TT-2194B | B | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2101B | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | PCS
23 | PI-2201B | PT-2201B | B | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B | 2" |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | Serial link | UCP-2101B | PCS
24 | PI-2210B | PT-2210B | B | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | Serial link | UCP-2101B | PCS
25 | PI-2211B | PT-2211B | B | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | Serial link | UCP-2101B | PCS
26 | PI-2200B | PT-2200B | B | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | HOLD |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
27 | LI-2200B | LT-2200B | B | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-300 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200B |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
28 | TI-2203B | TT-2203B | B | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AIR | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
29 | TI-2214B | TT-2214B | B | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2214B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
30 | TI-2215B | TT-2215B | B | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2215B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
31 | TI-2216B | TT-2216B | B | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | JBU-A-2101B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | TI-2216B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
32 | TI-2217B | TT-2217B | B | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | JBU-A-2101B | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | TI-2217B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
33 | TI-2218B | TT-2218B | B | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | JBU-A-2101B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | TI-2218B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
34 | TI-2219B | TT-2219B | B | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | JBU-A-2101B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | TI-2219B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
35 | TI-2220B | TT-2220B | B | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | JBU-A-2101B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | TI-2220B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
36 | FI-2206B | FT-2206B | B | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AI | JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-20000 | m3/h |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | PCS
37 | PI-2204B | PT-2204B | B | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 2" |  |  | AIR | JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
38 | TI-2204B | TT-2204B | B | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 4" |  |  | AI | JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
39 | PDI-2204B | PDT-2204B | B | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 1" |  |  | AI | JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | PCS
-
40 | PI-2220B | PT-2220B | B | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AIR | JBU-A-2103B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | PCS
41 | PI-2221B | PT-2221B | B | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AI | JBU-A-2103B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2221B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | PCS
42 | LI-2213B | LT-2213 A | B | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | AIR | JBU-A-2103B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213B |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | PCS
43 | TI-2213B | TT-2213B | B | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | AIR | JBU-A-2103B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | PCS
44 | VI-2200B | VT-2200B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | JBU-A-2104B | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | VI-2200B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
45 | VI-2201B | VT-2201B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | JBU-A-2104B | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | VI-2201B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
45 | VI-2202B | VT-2202B | B | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | JBU-A-2104B | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B
|  | VI-2202B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
46 | ZI-2200B | ZT-2200B | B | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200B |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
47 | ZI-2201B | ZT-2201B | B | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201B |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
48 | XI-2200B | XT-2200B | B | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200B |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
49 | TI-2222B | TE-2222B | B | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B |  |  | 4-20mA
|  | TI-2222B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
50 | TI-2225B | TE-2225B | B | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B |  |  | 4-20mA
|  | TI-2225B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
51 | TI-2228B | TE-2228B | B | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B |  |  | 4-20mA
|  | TI-2228B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | PCS
52 | TI-2191B | TS-2191B | B | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | JBU-D-2101B | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 0-200 | °C
|  | TI-2191B |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | DIRF | Trip Relay UCP A | UCP-2101B | 24VDC
|  | TA-2191B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | PCS | 24VDC
53 | TI-2194B | TS-2194B | B | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 0-200 | °C
|  | TI-2194B |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B
|  | TA-2194B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | PCS | 24VDC
54 | PI-2133B | PS-2133B | B | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | - | JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 0-80 | BARG
|  | PI-2133B |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B
|  | PA-2133B |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | PCS | 24VDC
55 | PI-2204B | PS-2204B | B | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | JBU-D-2101B | Trip Relay UCP A |  |  |  | N'IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204B |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B
|  | PA-2204B |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | Serial link | UCP-2101B | PCS | 24VDC
56 | PI-2220B | PS-2220B | B | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | - | JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 0-10 | BARG
|  | PI-2220B |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B
|  | PA-2220B |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | PCS | 24VDC
57 | XSS-2200B | XSS-2200B | B | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
58 | XSP-2200B | XSP-2200B | B | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
59 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
60 | XR-2200B | XR-2200B | B | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
61 | XF-2200B | XF-2200B | B | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSS-2201B | XSS-2201B | B | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | XSP-2201B | XSP-2201B | B | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
64 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XR-2201B | XR-2201B | B | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XF-2201B | XF-2201B | B | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSS-2202B | XSS-2202B | B | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
68 | XSP-2202B | XSP-2202B | B | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
69 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XR-2202B | XR-2202B | B | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XF-2202B | XF-2202B | B | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2203B | XSP-2203B | B | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
73 | XSS-2203B | XSS-2203B | B | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XR-2203B | XR-2203B | B | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XF-2203B | XF-2203B | B | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | XSS-2205B | XSS-2205B | B | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XSP-2205B | XSP-2205B | B | STOP COMMAND LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
79 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XR-2205B | XR-2205B | B | RUNNING STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XF-2205B | XF-2205B | B | FAILURE STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
82 | XSS-2220B | XSS-2220B | B | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XSP-2220B | XSP-2220B | B | STOP COMMAND WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
84 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XR-2220B | XR-2220B | B | RUNNING STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XF-2220B | XF-2220B | B | FAILURE STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
87 | XSS-2221B | XSS-2221B | B | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XSP-2221B | XSP-2221B | B | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
89 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XR-2221B | XR-2221B | B | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XF-2221B | XF-2221B | B | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
92 | XSS-2222B | XSS-2222B | B | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XSP-2222B | XSP-2222B | B | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
94 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XR-2222B | XR-2222B | B | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XF-2222B | XF-2222B | B | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
97 | XSS-2223B | XSS-2223B | B | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XSP-2223B | XSP-2223B | B | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
99 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XR-2223B | XR-2223B | B | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XF-2223B | XF-2223B | B | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
102 | XSS-2224B | XSS-2224B | B | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XSP-2224B | XSP-2224B | B | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
104 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XR-2224B | XR-2224B | B | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XF-2224B | XF-2224B | B | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
107 | XSS-2225B | XSS-2225B | B | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XSP-2225B | XSP-2225B | B | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
109 | USD-I-60B | USD-I-60B | B | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XR-2225B | XR-2225B | B | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XF-2225B | XF-2225B | B | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
112 |  | HST-2230B | B | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 |  | HSP-2230B | B | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 |  | HSL-2230B | B | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 |  | HSR-2230B | B | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 |  | HST-2231B | B | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
117 |  | HSP-2231B | B | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 |  | HSL-2231B | B | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 |  | HSR-2231B | B | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 |  | HST-2232B | B | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 |  | HSP-2232B | B | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
122 |  | HSL-2232B | B | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 |  | HSR-2232B | B | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
124 |  | HST-2233B | B | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2233B | B | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2233B | B | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2233B | B | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2234B | B | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2234B | B | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2234B | B | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2234B | B | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2235B | B | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2235B | B | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2235B | B | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2235B | B | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2236B | B | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2236B | B | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2236B | B | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2236B | B | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HSL-2237B | B | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HST-2237B | B | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSP-2237B | B | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2237B | B | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2239B | B | PUSH BUTTON | WATER COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2239B | B | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2239B | B | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2239B | B | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2240B | B | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2240B | B | PUSH BUTTON | BARRING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2240B | B | SELECTOR SWITCH | BARRING MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2240B | B | SELECTOR SWITCH | BARRING MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HST-2242B | B | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HSP-2242B | B | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSL-2242B | B | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSR-2242B | B | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HST-2243B | B | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSP-2243B | B | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2243B | B | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2243B | B | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HSL-2241B | B | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSR-2241B | B | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSR-2242B | B | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HST-2241B | B | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | ESDL-2230B | B | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DIRF | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSL-2242B1 | B | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HSL-2242B2 | B | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSL-2242B3 | B | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2242B4 | B | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSL-2242B5 | B | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | XR-2230B | B | SIGNAL LAMP | OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | XR-2231B | B | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | XR-2232B | B | SIGNAL LAMP | LUBRICATOR HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | XR-2233B | B | SIGNAL LAMP | LUBRICATOR MOTOR ACTIVE LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | XR-2234B | B | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | XR-2235B | B | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | XR-2236B | B | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | XR-2237B | B | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | XR-2238B | B | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | XR-2239B | B | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | XR-2240B | B | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | XR-2242B | B | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101B | AK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | XR-2243B | B | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101B | AK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | XSP-2230B | B | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XF-2230B | B | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | ESDL-2230B | B | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 | PSOV-2121B | PSOV-2121B | B | ON OFF VALVE SOLENOID | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DOR | UCP-2101B | JBU-S-2101 | 24VDC | W | 24VDC | NIS | FO | [9 empty] | Valve is in client scope of supply
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
187 | XZIC-2121B | XZIC-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | JBU-D-2101 | UCP-2101B | 24VDC | W | 24VDC | NIS
188 | XZIO-2121B | XZIO-2121B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | JBU-D-2101 | UCP-2101B | 24VDC | W | 24VDC | NIS
189 | PSOV-2233B | PSOV-2233B | B | ON OFF VALVE SOLENOID | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DOR | UCP-2101B | FIELD | 24VDC | W | 24VDC | NIS | FO
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
190 | XZIC-2133B | XZIC-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | FIELD | UCP-2101B | 24VDC | W | 24VDC | NIS
191 | XZIO-2133B | XZIO-2133B | B | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1B |  |  |  | DI | FIELD | UCP-2101B | 24VDC | W | 24VDC | NIS
192 |  | ESD-01B | B | ESD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIRF | ESD | UCP-2101B | 24VDC | W | 24VDC | NIS
193 |  | ESD-02B | B | ESD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIRF | ESD | UCP-2101B | 24VDC | W | 24VDC | NIS
194 |  | ESD-02 | B | ESD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIRF | ESD | UCP-2101B | 24VDC | W | 24VDC | NIS
195 |  | USD-05B | B | ESD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DOR | UCP-2101B | ESD | 24VDC | D | 24VDC | NIS
196 |  | PT-2121B | B | SPILL BACK |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | AIR | FCS | UCP-2101B | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
197 |  | XS-2100B | B | Time Syc |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DI | FCS | UCP-2101B | 24VDC | W | 24VDC | NIS
198 |  | HSS-2125B | B | Permission to start |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIR | FCS | UCP-2101B | 24VDC | W | 24VDC | NIS
199 |  | HSS-2123B | B | Command Start |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIR | FCS | UCP-2101B | 24VDC | W | 24VDC | NIS
200 |  | HSP-2123B | B | Command Stop |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIR | FCS | UCP-2101B | 24VDC | W | 24VDC | NIS
201 |  | HSS-2124B | B | Ready to Start |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DO | UCP-2101B | FCS | 24VDC | D | 24VDC | NIS
202 |  | XR-2121B | B | Running Status |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DO | UCP-2101B | FCS | 24VDC | D | 24VDC | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 29 | 5.8 | 35
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 11 | 2.2 | 14
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 83 | 16.6 | 100
|  |  | 6 | DIR | 3 | 0.6 | 4
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 21 | 4.2 | 26
|  |  | 9 | DOR | 31 | 6.2 | 37
V02
V02
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
Note on B164: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C164: Forouzandeh Fatemeh: ALARM L,H چک شود

## LIST-C
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 27 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V01
Item No. |  |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201C | POSV-2201C | C | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
2 | POSV-2202C | POSV-2202C | C | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
3 | POSV-2203C | POSV-2203C | C | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
4 | POSV-2204C | POSV-2204C | C | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
5 | POSV-2205C | POSV-2205C | C | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DOR | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
6 | POSV-2123C | POSV-2123C | C | SOLENOID VALVE | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET1C |  |  |  | DOR | UCP-2101C | JBU-S-2103 | 24VDC | W |  | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
7 | CZSO-2123C | CZSO-2123C | C | LIMIT SWITCH | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET1C |  |  |  | DI | JBU-D-2103 | UCP-2101C | 24VDC | W |  | NIS
| CZSC-2123C | CZSC-2123C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET1C |  |  |  | DI | JBU-D-2103 | UCP-2101C | 24VDC | W |  | NIS
8 | FI-2121C | FT-2121C | C | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
9 | TI-2122C | TT-2122C | C | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-100 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
10 | PDI-2122C | PDT-2122C | C | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
11 | PI-2123C | PT-2123C | C | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-40 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
12 | TI-2123C | TT-2123C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
13 | PI-2124C | PT-2124C | C | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
14 | FI-2131C | FT-2131C | C | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-8668 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
15 | TI-2132C | TT-2132C | C | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
16 | PI-2132C | PT-2132C | C | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
17 | PDI-2132C | PDT-2132C | C | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-0.6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
18 | TI-2133C | TT-2133C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
19 | PI-2133C | PT-2133C | C | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2103 | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-80 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
20 | PCY-2123C | PCY-2123C | C | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AOR | UCP-2101C | JBU-A-2103 |  |  | 4-20mA | IS
|  | PCYZ-2123C |  | Feed back |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2103 | UCP-2101C |  |  | 4-20mA | IS
|  | PCYZI-2123C |  | Feed back |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS |  |  | 4-20mA | IS
21 | TI-2191C | TT-2191C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
22 | TI-21941C | TT-2194C | C | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2101C | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | PCS
23 | PI-2201C | PT-2201C | C | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C | 2" |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | Serial link | UCP-2101C | PCS
24 | PI-2210C | PT-2210C | C | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | Serial link | UCP-2101C | PCS
25 | PI-2211C | PT-2211C | C | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | Serial link | UCP-2101C | PCS
26 | PI-2200C | PT-2200C | C | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | HOLD |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
27 | LI-2200C | LT-2200C | C | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-300 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200C |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
28 | TI-2203C | TT-2203C | C | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
29 | TI-2214C | TT-2214C | C | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2214C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
30 | TI-2215C | TT-2215C | C | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC |  | 4-20mA Hart | IS |  | 0-120 | °C
|  | TI-2215C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
31 | TI-2216C | TT-2216C | C | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | JBU-A-2101C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | TI-2216C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
32 | TI-2217C | TT-2217C | C | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | JBU-A-2101C | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | TI-2217C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
33 | TI-2218C | TT-2218C | C | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | JBU-A-2101C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | TI-2218C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
34 | TI-2219C | TT-2219C | C | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | JBU-A-2101C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | TI-2219C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
35 | TI-2220C | TT-2220C | C | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | JBU-A-2101C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | TI-2220C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
36 | FI-2206C | FT-2206C | C | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-20000 | m3/h |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | PCS
37 | PI-2204C | PT-2204C | C | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 2" |  |  | AIR | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
38 | TI-2204C | TT-2204C | C | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 4" |  |  | AI | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
39 | PDI-2204C | PDT-2204C | C | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 1" |  |  | AI | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | PCS
-
40 | PI-2220C | PT-2220C | C | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AIR | JBU-A-2103C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | PCS
41 | PI-2221C | PT-2221C | C | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AI | JBU-A-2103C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2221C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | PCS
42 | LI-2213C | LT-2213 A | C | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | AIR | JBU-A-2103C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213C |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | PCS
43 | TI-2213C | TT-2213C | C | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | AIR | JBU-A-2103C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | PCS
44 | VI-2200C | VT-2200C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | JBU-A-2104C | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | VI-2200C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
45 | VI-2201C | VT-2201C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | JBU-A-2104C | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | VI-2201C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
45 | VI-2202C | VT-2202C | C | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | JBU-A-2104C | Trip Relay UCP | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C
|  | VI-2202C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
46 | ZI-2200C | ZT-2200C | C | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200C |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
47 | ZI-2201C | ZT-2201C | C | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201C |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
48 | XI-2200C | XT-2200C | C | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200C |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
49 | TI-2222C | TE-2222C | C | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C |  |  | 4-20mA
|  | TI-2222C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
50 | TI-2225C | TE-2225C | C | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C |  |  | 4-20mA
|  | TI-2225C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
51 | TI-2228C | TE-2228C | C | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C |  |  | 4-20mA
|  | TI-2228C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | PCS
52 | TI-2191C | TS-2191C | C | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 0-200 | °C
|  | TI-2191C |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | DIRF | Trip Relay UCP A | UCP-2101C | 24VDC
|  | TA-2191C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | PCS | 24VDC
53 | TI-2194C | TS-2194C | C | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 0-200 | °C
|  | TI-2194C |  | TEMPERATURE INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C
|  | TA-2194C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | PCS | 24VDC
54 | PI-2133C | PS-2133C | C | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 0-80 | BARG
|  | PI-2133C |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C
|  | PA-2133C |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | PCS | 24VDC
55 | PI-2204C | PS-2204C | C | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | N'IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204C |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C
|  | PA-2204C |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | Serial link | UCP-2101C | PCS | 24VDC
56 | PI-2220C | PS-2220C | C | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 0-10 | BARG
|  | PI-2220C |  | PRESSURE INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C
|  | PA-2220C |  | PRESSURE Trip HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | PCS | 24VDC
57 | XSS-2200C | XSS-2200C | C | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
58 | XSP-2200C | XSP-2200C | C | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
59 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
60 | XR-2200C | XR-2200C | C | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
61 | XF-2200C | XF-2200C | C | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSS-2201C | XSS-2201C | C | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | XSP-2201C | XSP-2201C | C | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
64 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XR-2201C | XR-2201C | C | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XF-2201C | XF-2201C | C | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSS-2202C | XSS-2202C | C | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
68 | XSP-2202C | XSP-2202C | C | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
69 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XR-2202C | XR-2202C | C | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XF-2202C | XF-2202C | C | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2203C | XSP-2203C | C | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
73 | XSS-2203C | XSS-2203C | C | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XR-2203C | XR-2203C | C | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XF-2203C | XF-2203C | C | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | XSS-2205C | XSS-2205C | C | START COMMAND LUB OIL COOLER | LUB OIL COOLER (AE-2101-OC A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XSP-2205C | XSP-2205C | C | STOP COMMAND LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
79 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XR-2205C | XR-2205C | C | RUNNING STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XF-2205C | XF-2205C | C | FAILURE STATUS LUB OIL COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
82 | XSS-2220C | XSS-2220C | C | START COMMAND WATER CONSULE COOLER | WATER CONSULE COOLER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XSP-2220C | XSP-2220C | C | STOP COMMAND WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
84 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XR-2220C | XR-2220C | C | RUNNING STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XF-2220C | XF-2220C | C | FAILURE STATUS WATER CONSULE COOLER |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
87 | XSS-2221C | XSS-2221C | C | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XSP-2221C | XSP-2221C | C | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
89 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XR-2221C | XR-2221C | C | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XF-2221C | XF-2221C | C | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
92 | XSS-2222C | XSS-2222C | C | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XSP-2222C | XSP-2222C | C | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
94 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XR-2222C | XR-2222C | C | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XF-2222C | XF-2222C | C | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
97 | XSS-2223C | XSS-2223C | C | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (AE-2101-WC A) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XSP-2223C | XSP-2223C | C | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
99 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XR-2223C | XR-2223C | C | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XF-2223C | XF-2223C | C | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
102 | XSS-2224C | XSS-2224C | C | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XSP-2224C | XSP-2224C | C | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
104 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XR-2224C | XR-2224C | C | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XF-2224C | XF-2224C | C | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
107 | XSS-2225C | XSS-2225C | C | START COMMAND | MOTOR BEARING DEVICE MOTOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XSP-2225C | XSP-2225C | C | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
109 | USD-I-60C | USD-I-60C | C | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XR-2225C | XR-2225C | C | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XF-2225C | XF-2225C | C | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
112 |  | HST-2230C | C | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 |  | HSP-2230C | C | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 |  | HSL-2230C | C | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 |  | HSR-2230C | C | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 |  | HST-2231C | C | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
117 |  | HSP-2231C | C | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 |  | HSL-2231C | C | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 |  | HSR-2231C | C | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 |  | HST-2232C | C | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 |  | HSP-2232C | C | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
122 |  | HSL-2232C | C | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 |  | HSR-2232C | C | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
124 |  | HST-2233C | C | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2233C | C | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2233C | C | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2233C | C | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2234C | C | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2234C | C | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2234C | C | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2234C | C | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2235C | C | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2235C | C | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2235C | C | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2235C | C | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2236C | C | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2236C | C | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2236C | C | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2236C | C | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HSL-2237C | C | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HST-2237C | C | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSP-2237C | C | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2237C | C | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2239C | C | PUSH BUTTON | WATER COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2239C | C | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2239C | C | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2239C | C | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2240C | C | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2240C | C | PUSH BUTTON | BARRING MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2240C | C | SELECTOR SWITCH | BARRING MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2240C | C | SELECTOR SWITCH | BARRING MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HST-2242C | C | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HSP-2242C | C | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSL-2242C | C | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSR-2242C | C | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HST-2243C | C | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSP-2243C | C | PUSH BUTTON | WATER COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2243C | C | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2243C | C | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HSL-2241C | C | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSR-2241C | C | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSR-2242C | C | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HST-2241C | C | PUSH BUTTON | LAMP TEST PUSHBUTTON SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | ESDL-2230C | C | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DIRF | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSL-2242C1 | C | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HSL-2242C2 | C | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSL-2242C3 | C | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2242C4 | C | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSL-2242C5 | C | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | XR-2230C | C | SIGNAL LAMP | OIL HEATER ON LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | XR-2231C | C | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR START LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | XR-2232C | C | SIGNAL LAMP | LUBRICATOR HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | XR-2233C | C | SIGNAL LAMP | LUBRICATOR MOTOR ACTIVE LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | XR-2234C | C | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | XR-2235C | C | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | XR-2236C | C | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | XR-2237C | C | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | XR-2238C | C | SIGNAL LAMP | WATER HEATER ACTIVE LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | XR-2239C | C | SIGNAL LAMP | WATER COOLER RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | XR-2240C | C | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | XR-2242C | C | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101C | AK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | XR-2243C | C | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101C | AK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | XSP-2230C | C | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XF-2230C | C | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | ESDL-2230C | C | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 | PSOV-2121C | PSOV-2121C | C | ON OFF VALVE SOLENOID | INPUT ON OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DOR | UCP-2101C | JBU-S-2101 | 24VDC | W | 24VDC | NIS | FO | [9 empty] | Valve is in client scope of supply
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
187 | XZIC-2121C | XZIC-2121C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | JBU-D-2101 | UCP-2101C | 24VDC | W | 24VDC | NIS
188 | XZIO-2121C | XZIO-2121C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | JBU-D-2101 | UCP-2101C | 24VDC | W | 24VDC | NIS
189 | PSOV-2233C | PSOV-2233C | C | ON OFF VALVE SOLENOID | OUTPUT OFF VALVE(CLINET SIDE) | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DOR | UCP-2101C | FIELD | 24VDC | W | 24VDC | NIS | FO
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  |  | Trip Relay UCP A | JBU-S-2101 | 24VDC | W | NO | NIS
190 | XZIC-2133C | XZIC-2133C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | FIELD | UCP-2101C | 24VDC | W | 24VDC | NIS
191 | XZIO-2133C | XZIO-2133C | C | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0006-SHEET 1C |  |  |  | DI | FIELD | UCP-2101C | 24VDC | W | 24VDC | NIS
192 |  | ESD-01C | C | ESD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIRF | ESD | UCP-2101C | 24VDC | W | 24VDC | NIS
193 |  | ESD-02C | C | ESD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIRF | ESD | UCP-2101C | 24VDC | W | 24VDC | NIS
194 |  | ESD-02 | C | ESD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIRF | ESD | UCP-2101C | 24VDC | W | 24VDC | NIS
195 |  | USD-05C | C | ESD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DOR | UCP-2101C | ESD | 24VDC | D | 24VDC | NIS
196 |  | PT-2121C | C | SPILL BACK |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | AIR | FCS | UCP-2101C | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
197 |  | XS-2100C | C | Time Syc |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DI | FCS | UCP-2101C | 24VDC | W | 24VDC | NIS
198 |  | HSS-2125C | C | Permission to start |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIR | FCS | UCP-2101C | 24VDC | W | 24VDC | NIS
199 |  | HSS-2123C | C | Command Start |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIR | FCS | UCP-2101C | 24VDC | W | 24VDC | NIS
200 |  | HSP-2123C | C | Command Stop |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIR | FCS | UCP-2101C | 24VDC | W | 24VDC | NIS
201 |  | HSS-2124C | C | Ready to Start |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DO | UCP-2101C | FCS | 24VDC | D | 24VDC | NIS
202 |  | XR-2121C | C | Running Status |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DO | UCP-2101C | FCS | 24VDC | D | 24VDC | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 29 | 5.8 | 35
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 11 | 2.2 | 14
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 83 | 16.6 | 100
|  |  | 6 | DIR | 3 | 0.6 | 4
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 21 | 4.2 | 26
|  |  | 9 | DOR | 31 | 6.2 | 37
V02
V02
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
V01
Note on B164: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C164: Forouzandeh Fatemeh: ALARM L,H چک شود