## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-DS-0005
Document Title:CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-SVTR-HY-0034 |  |  | Transmital Date:2024/02/06
[5 empty] | CRS No: NISOC-CRS-BK-GCS-HY-120-IN-DS-0005_V02 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 02/2294/338516 | 1402/08/23 | بر اساس بررسی انجام شده ،تامین تابلو با ضخامت 3 میلیمتر برای امکان پذیر نیست. ماکزیمم ضخامت امکان پذیر 2.5mm می باشد. با توجه به محل نصب تابلو در ITR ضخامت ذکر شده می تواند با تایید کارفرمای محترم جواب گوی نیاز ایشان باشد. در صورتی که کارفرما محترم شرکت تابلو سازی را پیشنهاد دارد که توانایی تولید تابلو با ضخامت که با این مشخصات سراغ دارد اعلام نماید ما از ایشان تامین کنیم.
2 |  |  | 02/2294/338516 | 1402/08/23 | با Note1 &2 مشخص شده است Note1: Monitoring of machinery will be done by PLC. PLC is high available & high reliability Note 2: As per configuration document , ESD system is realy base included in PLC panel
3 |  |  | 02/2294/338516 | 1402/08/23 | مورد تایید است . در مدرک Configuration بریرهای قسمت Relay center از D5254S به D1054S تغییر یافت که Hart را ساپورت می کند. قسمت Barrier For Analog (Hart) در دیتاشیت تیک حورده است.
4 |  |  | 02/2294/338516 | 1402/08/23 | مورد تایید است .
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 17 Jul 2023 |  |  |  |  | Date: