## Cover
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES | [8 empty] | شماره صفحه: 1 از 4
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN | DS | 0005 | V04
طرح نگهداشت و افزایش تولید 27 مخزن
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES نگهداشت و افزایش تولید میدان نفتی بینک
V04 | May. 2024 | AFC |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V03 | Feb. 2024 | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V02 | Oct. 2023 | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V01 | Aug. 2023 | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | M.Mehrshad
V00 | Jun. 2023 | IFR |  |  |  | Havayar |  |  | M.Fakharian |  |  |  | M.Mehrshad
Rev. | Date | Purpose of Issue/Status |  |  |  | Prepared By |  |  | Checked By |  |  |  | Approved By | Client Approval

## Index
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES | [11 empty] | شماره صفحه: 2 از 4
[5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | HY | 120 | IN | DS |  | 0005 |  | V04
Tabulation Of Revised Pages
| Page | V00 | V01 | V02 |  | V03 |  | V04 |  |  | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | X | X | X |  | X |  | X |  |  | 36
| 2 | X | X | X |  | X |  | X |  |  | 37
| 3 | X | X | X |  | X |  | X |  |  | 38
| 4 |  | X | X |  | X |  | X |  |  | 39
| 5 | [9 empty] | 40
| 6 | [9 empty] | 41
| 7 | [9 empty] | 42
| 8 | [9 empty] | 43
| 9 | [9 empty] | 44
| 10 | [9 empty] | 45
| 11 | [9 empty] | 46
| 12 | [9 empty] | 47
| 13 | [9 empty] | 48
| 14 | [9 empty] | 49
| 15 | [9 empty] | 50
| 16 | [9 empty] | 51
| 17 | [9 empty] | 52
| 18 | [9 empty] | 53
| 19 | [9 empty] | 54
| 20 | [9 empty] | 55
| 21 | [9 empty] | 56
| 22 | [9 empty] | 57
| 23 | [9 empty] | 58
| 24 | [9 empty] | 59
| 25 | [9 empty] | 60
| 26 | [9 empty] | 61
| 27 | [9 empty] | 62
| 28 | [9 empty] | 63
| 29 | [9 empty] | 64
| 30 | [9 empty] | 65
| 31 | [9 empty] | 66
| 32 | [9 empty] | 67
| 33 | [9 empty] | 68
| 34 | [9 empty] | 69
| 35 | [9 empty] | 70

## Data sheet
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES
شماره پیمان: 9184 – 073 - 053 | [5 empty] | Project |  | Package |  |  | Issuer |  | Facility |  | Dicipline |  |  | Doc. | Sequence |  | Rev | شماره صفحه: 3 از 4
[6 empty] | BK |  | GCS |  |  | HY |  | 120 |  | IN |  |  | DS | 0005 |  | V04
Tag Number
UCP-2101A UCP-2101B UCP-2101C
Standards and regulations
¢ | IEC | [6 empty] | ¢ | IPS | [9 empty] | £ | RITAL
Panel data
Panel type |  |  |  |  | £ | Rittal brand | [5 empty] | ¢ | Rittal type(Made in Iran) | [9 empty] | £ | Rack mounted
[5 empty] | £ | Plug-in design | [5 empty] | £ | Wall/skid Mounted
[5 empty] | £ | Fixed | [5 empty] | ¢ | Free Standing
Installation |  |  |  |  | ¢ | Indoor (Client control room) | [5 empty] | £ | Outdoor under shelter | [9 empty] | £ | Outdoor unsheltered
Color of enclosure |  |  |  |  | £ | RAL 7032 | [5 empty] | ¢ | RAL 7035 | [9 empty] | £ | Other
Dimensions |  |  |  |  | Width |  |  | 2400(3*800mm) |  |  | mm |  | Height |  |  | 2100 |  |  |  | mm |  | Depth |  |  | 800mm
Body material & size |  |  |  |  | Material |  |  | Sheet Steel |  |  | - |  | Thickness |  |  | 2 |  |  |  | mm
Door & Top material & size |  |  |  |  | Material |  |  | Sheet Steel |  |  | - |  | Thickness |  |  | 2 |  |  |  | mm
Cable connection location |  |  |  |  | ¢ | Bottom |  | £ | Top
Environmental conditions
Humidity range |  |  |  |  | £ | 0-10% |  |  | £ | 10-30% |  | £ | 30-50% |  |  | £ | 50-60% |  |  | ¢ | 60-70% |  |  | £ | 70-80%
Substation temperature (max) |  |  |  |  | £ | 25°C |  |  | £ | 30°C |  | £ | 35°C |  |  | ¢ | 43°C |  |  | £ | 44°C |  |  | £ | 50°C
Substation temperature (min) |  |  |  |  | £ | + 1 °C |  |  | ¢ | 0 °C |  | £ | -20 °C
Installation altitude above MSL |  |  |  |  | £ | sea level |  |  | ¢ | ≤1500m |  | £ | >1000m |  |  |  | >2000m
Ingress of protection |  |  |  |  | £ | IP31 |  |  | £ | IP40 |  | £ | IP41 |  |  | £ | IP42 |  |  | ¢ | IP54 |  |  | £ | IP65
Control cabinet heating / cooling |  |  |  |  | ¢ | Ventilated | [5 empty] | £ | Unventilated
[5 empty] | ¢ | Heater & Thermostat | [5 empty] | ¢ | Fan & Filter | [6 empty] | ¢ | Hydrostat |  |  |  |  | £ | None
Lighting |  |  |  |  | ¢ | Florsant | [5 empty] | ¢ | Microswitch | [6 empty] | ¢ | socket |  |  |  |  | £ | Other
Earth |  |  |  |  | ¢ | Instrument Earth (IS & NIS) | [5 empty] | ¢ | Electrical Earth
PLC data
Brand / type | [8 empty] | Siemens | [14 empty] | Other
[9 empty] | S7 - 1200 |  |  | S7-300 |  |  |  | S7- 400FH |  |  |  | Other
Redundancy | [8 empty] | No Redundancy |  |  | CPU |  |  |  | Communication |  |  |  | Powersupply |  |  |  | Critical I/O (I/O in ET200M)
HMI Type | [8 empty] | None |  |  | TP177A |  |  |  | TP177B |  |  |  | MP-277 # 19" |  |  |  | TP1500 (15")
Barrier For Analog (Hart) | [8 empty] | Yes |  |  | NO
Note1: Monitoring of machinery will be done by PLC. PLC is high available & high reliability.
Note 2: As per configuration document , ESD system is realy base included in PLC panel.
Soft ware Data for Laptop
Orginal license |  |  | Yes | No |  |  |  | Orginal software |  |  | Yes |  |  | No |  |  | Logic source |  | Yes |  | No | One Laptop(EWS)/One IPC(OWS) Yes |  |  |  |  | No
Certificate |  |  | SIL Certificate for Barrier GMI & Relay Trip signal
Panel IP
Used Instruments | [14 empty] | Communication | [5 empty] | Other devices
no. | Qty. | instrument |  |  |  |  | Description | [8 empty] | None | [5 empty] | Control relay
Quantity of I/O module as per below document: BK-GCS-HY-120-IN-DG-0001 PLC WIRING DIAGRAM & TERMINAL DETAILS BK-GCS-HY-120-IN-DG-0002 CONTROL SYSTEM CABINETS AND CONSOLES LAYOUT DRAWING Reference Document: BK-GCS-HY-120-IN-DG-0002 OVERAL CONTROL/SAFETY SYSTEM CONFIGURATION DIAGRAM BK-GCS-HY-120-PR-PI-0001 P&ID Diagram BK-GCS-HY-120-IN-LI-0005 I/O List | [15 empty] | PRO-FI Bus module For DCS | [5 empty] | Annunciator
[16 empty] | Modbus RTU module For DCS | [5 empty] | Selectors (UCP/DCS Selector mode & Load Selector switch)
[16 empty] | PLC communication (with hard wire To DCS) | [5 empty] | Push button (Compressor Start & Stop)
[16 empty] | Hard wire for field | [5 empty] | Indicator light
[16 empty] | Ethernet ( WIRE ) to IPC | [5 empty] | Terminal
[15 empty] | Note: | Some Signals between UCP and DCS are hard wire. | [5 empty] | MCB
Emergency stop
Supply voltage
Supply feeder : | [8 empty] | voltage Transformator |  |  |  |  | UPS ( Redundant dlivered by client) | [5 empty] | Normal (Fan & Lighting) | [5 empty] | Other
Voltage power rate for control panel : | [8 empty] | 24V DC |  |  |  |  | 110V AC | [5 empty] | 230V AC | [5 empty] | Other
[9 empty] | 50 Hz. |  |  |  |  | 60 Hz.
Voltage power rate for Instrumentation purposes : | [8 empty] | 24V DC |  |  |  |  | 230V AC | [5 empty] | 230V AC | [5 empty] | Other
Identification / Wiring / nameplate
Label & Name plate | [8 empty] | Label |  |  |  | Name plate |  |  |  |  | Wiring tag
Language | [8 empty] | Persian |  |  |  | English |  |  |  |  | Other
Insulation material of leads | [8 empty] | PVC |  |  |  | Flame retardant
Gland data for PLC panel
Material | [8 empty] | Brass nickel plated |  |  |  |  | Brass |  |  | thermoplastic | [5 empty] | S.S |  |  | other
Ingress of protection | [8 empty] | EExe |  | Eexd |  |  | IP54 |  |  | IP66 |  |  | IP68 |  |  | other
Mechanical protection | [8 empty] | Armoured |  |  |  |  | un-Armoured
V04
V03

## Data sheet (3)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  | Project | Package | Issuer | Facility | Dicipline |  | Doc. | Sequence | Rev | شماره صفحه: 4 از 4
|  |  | BK | GCS | HY | 120 | IN |  | DS | 0005 | V04
| Item | Description | [5 empty] | Order# (if applicable) |  |  |  | Manufacturer | Country of Origin
LAPTOP (EWS)
| 1 | PCS7 V9.1 | [5 empty] | N.A |  |  |  | Siemens | Germany
| 2 | Tia Portal V17 | [5 empty] | N.A |  |  |  | Siemens | Germany
| 3 | SIMATIC PCS 7, software, Software Media Package V9.1 SP1 data storage medium without license use only in connection with valid license Trial License for 14 days, without liability and warranty with restricted functionality (see product info) R-SW, software on USB without documentation 5 languages (de, en, fr, it, es), executable in Windows 10 LTSC 2019 Windows Server 2019 for more information, see PCS 7 V9.1 Readme reference hardware: PCS 7 IPC bundle ******************************* content: 1x USB | [5 empty] | 6ES7658‐4XX68‐0YT8 |  |  |  | Siemens | Germany
| 4 | SIMATIC PCS 7, software, AS/OS Engineering V9.1 Floating License for 1 user E-SW, without SW, without docu. license key on USB flash drive, class A, 5 languages (de, en, fr, it, sp), executable in WIN 10 LTSC 2019 WIN Server 2019 for further information, see PCS 7 V9.1 Readme reference HW: PCS 7 IPC bundle ******************************* content: 1x USB | [5 empty] | 6ES7658‐5AX68‐0YA5 |  |  |  | Siemens | Germany
| 5 | SIMATIC S7, SOFTWARE F SYSTEMS V6.2, FLOAT. LICENSE F.1 INSTALLATION R-SW, WITHOUT SW AND DOCU. LICENSE KEY ON USB STICK, CLASS A, 2 LANGUAGES (G,E), EXECUTABLE UNDER WIN7 SP1 / SERVER 2008 R2 SP1 OS ONLY: WIN10 / SERVER 2012 R2 REFERENCE-HW: PC/PG | [5 empty] | 6ES7833-1CC26-0YA5 |  |  |  | Siemens | Germany
| 6 | SIMATIC S7, software F-Systems V6.2 Update 1 Software Media Package Data medium without license usage only in connection with valid license E-SW / R-SW, SW and documentation on CD 2 languages (de, en), executable on WIN7 SP1 / Server 2008 R2 SP1/ WIN10 / Server 2012 R2/ Server 2016 Reference HW: PC/PG | [5 empty] | 6ES7833-4CC26-0YT8 |  |  |  | Siemens | Germany
OWS (IPC)
| 7 | SIMATIC PCS 7, software, OS Software Client V9.1 Floating License for 1 user R-SW, without SW, without docu. license key on USB flash drive, class A, 5 languages (de, en, fr, it, sp), executable in WIN 10 LTSC 2019 for further information, see PCS 7 V9.1 Readme reference HW: PCS 7 IPC bundle ******************************* content: 1x USB | [5 empty] | 6ES7658‐2CX68‐0YB5 |  |  |  | Siemens | Germany
HMI
| 8 | SIMATIC WinCC Comfort V17, engineering software in the TIA Portal; Floating License; software and documentation on DVD; license key on USB flash drive; class A; 6 languages: de,en,fr,es,it,zh; for configuration of SIMATIC Panels | [5 empty] | 6AV2101-0AA07-0AA5 |  |  |  | Siemens | Germany