## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-DS-0005
Document Title:CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-SVTR-HY-0061 |  |  | Transmital Date:2024/05/05
[5 empty] | CRS No:NISOC-CRS-BK-GCS-HY-120-IN-DS-0005_V03 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 02/2294/535696 | 1402/12/23 | طبق کامنت های قبلی ، بر اساس بررسی انجام شده ،تامین تابلو با ضخامت 3 میلیمتر برای امکان پذیر نیست. ماکزیمم ضخامت امکان پذیر 2mm می باشد. با توجه به محل نصب تابلو در ITR ضخامت ذکر شده می تواند با تایید کارفرمای محترم جواب گوی نیاز ایشان باشد. در صورت ساخت تابلو یا ضخامت بیشتر از 2mm وزن تابلو بسیار بالا می رود و این موضوع در حمل و جابجایی و نصب مشکل ساز خواهد شد.به علت بالا رفتن ضخامت ورق امکان صحیح نصب فیلتر و فن وجود نخواهد داشت. همچنین بالا رفتن ورق باعث سنگین شدن درب تابلو آسیب دیدن لولا می گردد. با توجه به اینکه شرکت های مشاور تاییدیه را منوط به تایید کارفرمای محترم نموده است خواهشمند است در این خصوص تایید را مبذول فرمایید.
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 17 Jul 2023 |  |  |  |  | Date: