## Cover
Binak Oil Field Development Project Reciprocating Sour Gas Compressors
ALARM & SET POINT LIST
Contract No: |  |  | Project |  | Package | Issuer | Facility |  | Dicipline | Doc. | Sequence | Rev |  | شماره صفحه: 1 از 5
053-073-9184 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 0004 | V01
طرح نگهداشت و افزایش تولید 27 مخزن
ALARM & SET POINT LIST
نگهداشت و افزایش تولید میدان نفتی بینک
V01 |  | MAY.2024 |  | IFR |  |  |  | HAVAYAR |  |  | M.Fakharian |  | S.Faramarzpour
V00 |  | FEB.2023 |  | IFR |  |  |  | HAVAYAR |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued ForApproval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Revision
Binak Oil Field Development Project Reciprocating Sour Gas Compressors
ALARM &SET POINT LIST
Contract No: 053-073-9184 |  |  | Project | Package |  | Issuer | Facility | Dicipline | Doc. | Sequence |  | Rev |  | شماره صفحه: 2 از 5
|  |  | BK | GCS |  | HY | 120 | IN | LI | 0004 |  | V01
REVISION RECORD SHEET
Page | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## LIST-A
Binak Oil Field Development Project Reciprocating Sour Gas Compressors
ALARM & SET POINT LIST
Contract No: |  | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence |  | Rev
Contract No: 053-073-9184 |  | BK | GCS | HY | 120 | IN | LI | 0004 |  | V01 |  |  |  |  | شماره صفحه: 3 از 5
Item No. | Tag Number | Description |  |  | Service 1 |  | P&ID NUMBER |  |  | set point | Alarm Action |  | Shut Down Action |  | Range | Eng. Units | Remark
[9 empty] | Operating/Design |  | L | H | LL | HH
1 | PDT-2122A | DIFF PRESSURE TRANSMITTER |  |  | STRAINER FILTER SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
2 | PT-2123A | PRESSURE TRANSMITTER |  |  | 1st SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 4.9 / 24.5 | _ | 4 | 6 | _ | _ | 0-25 | BARG
3 | TT-2191A | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 37/180 | _ | _ | 140 | _ | _ | 0-200 | °C
4 | TS-2191A | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 37/180 | 150 | _ | _ | _ | 150 | 0-200 | °C
5 | PT-2124A | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 18 / 24.5 | _ | _ | 19 | _ | _ | 0-25 | BARG
6 | PDT-2132A | DIFF PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
7 | PT-2132A | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 17.1 / 24.5 | _ | 14.7 | _ | _ | _ | 0-25 | BARG
8 | TT-2194A | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 148/180 | _ | _ | 160 | _ | _ | 0-200 | °C
9 | TS-2194A | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 37/180 | 170 | _ | _ | _ | 170 | 0-200 | °C
10 | PT-2133A | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 54.9 / 62 | _ | _ | 56 | _ | _ | 10-100 | BARG
11 | PS-2133A | PRESSURE SWITCH |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 54.9/62 | 57 | _ | _ | _ | 57 | 10-100 | BARG
12 | PT-2200A | PRESSURE TRANSMITTER |  |  | ON LUBRICATOR |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 4/10 | _ | 4 | _ | _ | _ | 0-10 | BARG
13 | LT-2200A | LEVEL TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 0/425 | _ | 32.25 | _ | _ | _ | 0-425 | mmH2O | start permission :37.5
14 | TT-2203A | TEMPERATURE TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 70/85 | _ | 15 | 35 | _ | _ | 0-120 | °C | Stop/Start Heater Crank Case start permission:15
15 | PT-2204A | PRESSURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 6/10 | _ | 1.5 | 5 | _ | _ | 0-10 | BARG | start permission :5
16 | PS-2204A | PRESSURE SWITCH |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 5/10 | 1.2 | _ | _ | 1.2 | _ | 0-10 | BARG
17 | TT-2204A | TEMPERATURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 60/85 | _ | 5 | 65 | _ | _ | 0-120 | °C | start permission :36
18 | PDT-2204A | DIFF PRESSURE TRANSMITTER |  |  | LUBE OIL FILTER |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 0.1 / 0.5 | _ | _ | 0.7 | _ | _ | 0-1 | BARG
19 | PT-2210A | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 2.2 / 5 | _ | 1.2 | _ | _ | _ | 0-6 | BARG | start permission :2.2
20 | PT-2211A | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 1 / 5 | _ | 0.2 | _ | _ | _ | 0-6 | BARG | start permission :2
21 | PT-2212A | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | _ | _ | 4 | HAVAYAR | _ | 0-6 | BARG
22 | LT-2213A | LEVEL TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 0-1350 | _ | 500 | _ | 250 | _ | 0-1350 | mmH2O | LL: Main & Aux water pumps stop
23 | TT-2213A | TEMPERATURE TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 65/85 | _ | 60 | 63 | HAVAYAR | _ | 0-120 | °C | Stop/Start Heater Water Reservor
24 | PS-2220A | PRESSURE SWITCH |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 3/10 | 2 | _ | _ | 2 | _ | 0-10 | BARG
25 | PT-2220A | PRESSURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 3/10 | _ | 2.5 | 3 | _ | _ | 0-10 | BARG | Stop/Start Aux Water Pump start permission :3
26 | TT-2221A | TEMPERATURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 58/85 | _ | _ | 66 | _ | 70 | 0-120 | °C | start permission :60
|  | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
28 | VT-2201A | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
29 | VT-2202A | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
30 | ZT-2200A | ROD DROP TRANSMITTER |  |  | LEFT Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/4 | _ | _ | 0.6 | _ | _ | 4 | mm
31 | ZT-2201A | ROD DROP TRANSMITTER |  |  | Right Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/4 | _ | _ | 0.69 | _ | _ | 4 | mm
32 | TT-2214A | TEMPERATURE TRANSMITTER |  |  | MOTOR NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
33 | TT-2215A | TEMPERATURE TRANSMITTER |  |  | MOTOR DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
34 | TT-2216A | TEMPERATURE TRANSMITTER |  |  | COMP DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
35 | TT-2217A | TEMPERATURE TRANSMITTER |  |  | Right Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
36 | TT-2218A | TEMPERATURE TRANSMITTER |  |  | COMP NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
37 | TT-2219A | TEMPERATURE TRANSMITTER |  |  | LEFT Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
38 | TT-2220A | TEMPERATURE TRANSMITTER |  |  | COMP MID BEARING |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
39 | TE-2222A | TEMPERATURE ELEMET |  |  | MOTOR WINDING R |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
40 | TE-2225A | TEMPERATURE ELEMET |  |  | MOTOR WINDING S |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
41 | TE-2228A | TEMPERATURE ELEMET |  |  | MOTOR WINDING T |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
42 | XT-2200A | Rotation Speed |  |  | Rotation Speed |  | BK-GCS-HY-120-PR-PI-0001 7A |  | 0/500 | _ | _ | 430 | - | - | 0-500 | RPM
43 | PCV-2120A | PRESSURE REGULATOR |  |  | INSTRUMENT AIR |  | BK-GCS-HY-120-PR-PI-0001 3A |  | 6 / 12.5 | 6 | _ | _ | _ | _ | _ | BARG
44 | PCV-2205A | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 2.2 / 5 | 0.5 | _ | _ | _ | _ | _ | BARG
45 | PCV-2206A | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 2.2 / 5 | 2 | _ | _ | _ | _ | _ | BARG
46 | PCV-2201A | PRESSURE REGULATOR |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 6/10 | 6 | _ | _ | _ | _ | _ | BARG
47 | PSV-2132A | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
48 | PSV-2133A | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1A |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
49 | RV-2200A | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
50 | RV-2201A | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5A |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
51 | PSV-2203A | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG
52 | PSV-2204A | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4A |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG

## LIST-B
Binak Oil Field Development Project Reciprocating Sour Gas Compressors
ALARM & SET POINT LIST
Contract No: |  | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence |  | Rev
Contract No: 053-073-9184 |  | BK | GCS | HY | 120 | IN | LI | 0004 |  | V01 |  |  |  |  | شماره صفحه: 4 از 5
Item No. | Tag Number | Description |  |  | Service 1 |  | P&ID NUMBER |  |  | set point | Alarm Action |  | Shut Down Action |  | Range | Eng. Units | Remark
[9 empty] | Operating/Design |  | L | H | LL | HH
1 | PDT-2122B | DIFF PRESSURE TRANSMITTER |  |  | STRAINER FILTER SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
2 | PT-2123B | PRESSURE TRANSMITTER |  |  | 1st SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 4.9 / 24.5 | _ | 4 | 6 | _ | _ | 0-25 | BARG
3 | TT-2191B | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 37/180 | _ | _ | 140 | _ | _ | 0-200 | °C
4 | TS-2191B | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 37/180 | 150 | _ | _ | _ | 150 | 0-200 | °C
5 | PT-2124B | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 18 / 24.5 | _ | _ | 19 | _ | _ | 0-25 | BARG
6 | PDT-2132B | DIFF PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
7 | PT-2132B | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 17.1 / 24.5 | _ | 14.7 | _ | _ | _ | 0-25 | BARG
8 | TT-2194B | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 148/180 | _ | _ | 160 | _ | _ | 0-200 | °C
9 | TS-2194B | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 37/180 | 170 | _ | _ | _ | 170 | 0-200 | °C
10 | PT-2133B | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 54.9 / 62 | _ | _ | 56 | _ | _ | 10-100 | BARG
11 | PS-2133B | PRESSURE SWITCH |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 54.9/62 | 57 | _ | _ | _ | 57 | 10-100 | BARG
12 | PT-2200B | PRESSURE TRANSMITTER |  |  | ON LUBRICATOR |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 4/10 | _ | 4 | _ | _ | _ | 0-10 | BARG
13 | LT-2200B | LEVEL TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 0/425 | _ | 32.25 | _ | _ | _ | 0-425 | mmH2O | start permission :37.5
14 | TT-2203B | TEMPERATURE TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 70/85 | _ | 15 | 35 | _ | _ | 0-120 | °C | Stop/Start Heater Crank Case start permission:15
15 | PT-2204B | PRESSURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 6/10 | _ | 1.5 | 5 | _ | _ | 0-10 | BARG | start permission :5
16 | PS-2204B | PRESSURE SWITCH |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 5/10 | 1.2 | _ | _ | 1.2 | _ | 0-10 | BARG
17 | TT-2204B | TEMPERATURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 60/85 | _ | 5 | 65 | _ | _ | 0-120 | °C | start permission :36
18 | PDT-2204B | DIFF PRESSURE TRANSMITTER |  |  | LUBE OIL FILTER |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 0.1 / 0.5 | _ | _ | 0.7 | _ | _ | 0-1 | BARG
19 | PT-2210B | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 2.2 / 5 | _ | 1.2 | _ | _ | _ | 0-6 | BARG | start permission :2.2
20 | PT-2211B | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 1 / 5 | _ | 0.2 | _ | _ | _ | 0-6 | BARG | start permission :2
21 | PT-2212B | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | _ | _ | 4 | HAVAYAR | _ | 0-6 | BARG
22 | LT-2213B | LEVEL TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 0-1350 | _ | 500 | _ | 250 | _ | 0-1350 | mmH2O | LL: Main & Aux water pumps stop
23 | TT-2213B | TEMPERATURE TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 65/85 | _ | 60 | 63 | HAVAYAR | _ | 0-120 | °C | Stop/Start Heater Water Reservor
24 | PS-2220B | PRESSURE SWITCH |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 3/10 | 2 | _ | _ | 2 | _ | 0-10 | BARG
25 | PT-2220B | PRESSURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 3/10 | _ | 2.5 | 3 | _ | _ | 0-10 | BARG | Stop/Start Aux Water Pump start permission :3
26 | TT-2221B | TEMPERATURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 58/85 | _ | _ | 66 | _ | 70 | 0-120 | °C | start permission :60
|  | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
28 | VT-2201B | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
29 | VT-2202B | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
30 | ZT-2200B | ROD DROP TRANSMITTER |  |  | LEFT Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/4 | _ | _ | 0.6 | _ | _ | 4 | mm
31 | ZT-2201B | ROD DROP TRANSMITTER |  |  | Right Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/4 | _ | _ | 0.69 | _ | _ | 4 | mm
32 | TT-2214B | TEMPERATURE TRANSMITTER |  |  | MOTOR NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
33 | TT-2215B | TEMPERATURE TRANSMITTER |  |  | MOTOR DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
34 | TT-2216B | TEMPERATURE TRANSMITTER |  |  | COMP DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
35 | TT-2217B | TEMPERATURE TRANSMITTER |  |  | Right Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
36 | TT-2218B | TEMPERATURE TRANSMITTER |  |  | COMP NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
37 | TT-2219B | TEMPERATURE TRANSMITTER |  |  | LEFT Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
38 | TT-2220B | TEMPERATURE TRANSMITTER |  |  | COMP MID BEARING |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
39 | TE-2222B | TEMPERATURE ELEMET |  |  | MOTOR WINDING R |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
40 | TE-2225B | TEMPERATURE ELEMET |  |  | MOTOR WINDING S |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
41 | TE-2228B | TEMPERATURE ELEMET |  |  | MOTOR WINDING T |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
42 | XT-2200B | Rotation Speed |  |  | Rotation Speed |  | BK-GCS-HY-120-PR-PI-0001 7B |  | 0/500 | _ | _ | 430 | - | - | 0-500 | RPM
43 | PCV-2120B | PRESSURE REGULATOR |  |  | INSTRUMENT AIR |  | BK-GCS-HY-120-PR-PI-0001 3B |  | 6 / 12.5 | 6 | _ | _ | _ | _ | _ | BARG
44 | PCV-2205B | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 2.2 / 5 | 0.5 | _ | _ | _ | _ | _ | BARG
45 | PCV-2206B | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 2.2 / 5 | 2 | _ | _ | _ | _ | _ | BARG
46 | PCV-2201B | PRESSURE REGULATOR |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 6/10 | 6 | _ | _ | _ | _ | _ | BARG
47 | PSV-2132B | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
48 | PSV-2133B | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1B |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
49 | RV-2200B | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
50 | RV-2201B | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5B |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
51 | PSV-2203B | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG
52 | PSV-2204B | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4B |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG

## LIST-C
Binak Oil Field Development Project Reciprocating Sour Gas Compressors
ALARM & SET POINT LIST
Contract No: |  | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence |  | Rev
Contract No: 053-073-9184 |  | BK | GCS | HY | 120 | IN | LI | 0004 |  | V01 |  |  |  |  | شماره صفحه:5 از 5
Item No. | Tag Number | Description |  |  | Service 1 |  | P&ID NUMBER |  |  | set point | Alarm Action |  | Shut Down Action |  | Range | Eng. Units | Remark
[9 empty] | Operating/Design |  | L | H | LL | HH
1 | PDT-2122C | DIFF PRESSURE TRANSMITTER |  |  | STRAINER FILTER SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
2 | PT-2123C | PRESSURE TRANSMITTER |  |  | 1st SUCTION COMP |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 4.9 / 24.5 | _ | 4 | 6 | _ | _ | 0-25 | BARG
3 | TT-2191C | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 37/180 | _ | _ | 140 | _ | _ | 0-200 | °C
4 | TS-2191C | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 37/180 | 150 | _ | _ | _ | 150 | 0-200 | °C
5 | PT-2124C | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 1ST STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 18 / 24.5 | _ | _ | 19 | _ | _ | 0-25 | BARG
6 | PDT-2132C | DIFF PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 0.1 / 0.2 | _ | _ | 0.2 | _ | _ | 0-0.4 | BARG
7 | PT-2132C | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 17.1 / 24.5 | _ | 14.7 | _ | _ | _ | 0-25 | BARG
8 | TT-2194C | TEMPERATURE TRANSMITTER |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 148/180 | _ | _ | 160 | _ | _ | 0-200 | °C
9 | TS-2194C | TEMPERATURE SWITCH |  |  | ON DISCHARGE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 37/180 | 170 | _ | _ | _ | 170 | 0-200 | °C
10 | PT-2133C | PRESSURE TRANSMITTER |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 54.9 / 62 | _ | _ | 56 | _ | _ | 10-100 | BARG
11 | PS-2133C | PRESSURE SWITCH |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 54.9/62 | 57 | _ | _ | _ | 57 | 10-100 | BARG
12 | PT-2200C | PRESSURE TRANSMITTER |  |  | ON LUBRICATOR |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 4/10 | _ | 4 | _ | _ | _ | 0-10 | BARG
13 | LT-2200C | LEVEL TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 0/425 | _ | 32.25 | _ | _ | _ | 0-425 | mmH2O | start permission :37.5
14 | TT-2203C | TEMPERATURE TRANSMITTER |  |  | ON CRANK CASE |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 70/85 | _ | 15 | 35 | _ | _ | 0-120 | °C | Stop/Start Heater Crank Case start permission:15
15 | PT-2204C | PRESSURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 6/10 | _ | 1.5 | 5 | _ | _ | 0-10 | BARG | start permission :5
16 | PS-2204C | PRESSURE SWITCH |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 5/10 | 1.2 | _ | _ | 1.2 | _ | 0-10 | BARG
17 | TT-2204C | TEMPERATURE TRANSMITTER |  |  | ON LUBE OIL HEADER |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 60/85 | _ | 5 | 65 | _ | _ | 0-120 | °C | start permission :36
18 | PDT-2204C | DIFF PRESSURE TRANSMITTER |  |  | LUBE OIL FILTER |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 0.1 / 0.5 | _ | _ | 0.7 | _ | _ | 0-1 | BARG
19 | PT-2210C | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 2.2 / 5 | _ | 1.2 | _ | _ | _ | 0-6 | BARG | start permission :2.2
20 | PT-2211C | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | _ | 0.2 | _ | _ | _ | 0-6 | BARG | start permission :2
21 | PT-2212C | PRESSURE TRANSMITTER |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | _ | _ | 4 | HAVAYAR | _ | 0-6 | BARG
22 | LT-2213C | LEVEL TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 0-1350 | _ | 500 | _ | 250 | _ | 0-1350 | mmH2O | LL: Main & Aux water pumps stop
23 | TT-2213C | TEMPERATURE TRANSMITTER |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 65/85 | _ | 60 | 63 | HAVAYAR | _ | 0-120 | °C | Stop/Start Heater Water Reservor
24 | PS-2220C | PRESSURE SWITCH |  |  | WATER RESERVOIR |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 3/10 | 2 | _ | _ | 2 | _ | 0-10 | BARG
25 | PT-2220C | PRESSURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 3/10 | _ | 2.5 | 3 | _ | _ | 0-10 | BARG | Stop/Start Aux Water Pump start permission :3
26 | TT-2221C | TEMPERATURE TRANSMITTER |  |  | WATER TO CYLINDERS |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 58/85 | _ | _ | 66 | _ | 70 | 0-120 | °C | start permission :60
|  | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
28 | VT-2201C | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
29 | VT-2202C | VIBERATION TRANMITTER |  |  | FRAME VIBRATION |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/25.4 | _ | _ | 8 | _ | 12 | 25.4 | mm/SEC, RMS
30 | ZT-2200C | ROD DROP TRANSMITTER |  |  | LEFT Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/4 | _ | _ | 0.6 | _ | _ | 4 | mm
31 | ZT-2201C | ROD DROP TRANSMITTER |  |  | Right Cylinder Rod Drop Detector |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/4 | _ | _ | 0.69 | _ | _ | 4 | mm
32 | TT-2214C | TEMPERATURE TRANSMITTER |  |  | MOTOR NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
33 | TT-2215C | TEMPERATURE TRANSMITTER |  |  | MOTOR DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/95 | _ | _ | 90 | _ | 95 | 0-200 | °C
34 | TT-2216C | TEMPERATURE TRANSMITTER |  |  | COMP DE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
35 | TT-2217C | TEMPERATURE TRANSMITTER |  |  | Right Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
36 | TT-2218C | TEMPERATURE TRANSMITTER |  |  | COMP NDE BEARING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
37 | TT-2219C | TEMPERATURE TRANSMITTER |  |  | LEFT Cylinder PACKING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/130 | _ | _ | 120 | - | 130 | 0-200 | °C
38 | TT-2220C | TEMPERATURE TRANSMITTER |  |  | COMP MID BEARING |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/105 | _ | _ | 95 | - | 105 | 0-200 | °C
39 | TE-2222C | TEMPERATURE ELEMET |  |  | MOTOR WINDING R |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
40 | TE-2225C | TEMPERATURE ELEMET |  |  | MOTOR WINDING S |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
41 | TE-2228C | TEMPERATURE ELEMET |  |  | MOTOR WINDING T |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/145 | _ | _ | 135 | - | 145 | 0-200 | °C
42 | XT-2200C | Rotation Speed |  |  | Rotation Speed |  | BK-GCS-HY-120-PR-PI-0001 7C |  | 0/500 | _ | _ | 430 | - | - | 0-500 | RPM
43 | PCV-2120C | PRESSURE REGULATOR |  |  | INSTRUMENT AIR |  | BK-GCS-HY-120-PR-PI-0001 3C |  | 6 / 12.5 | 6 | _ | _ | _ | _ | _ | BARG
44 | PCV-2205C | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 2.2 / 5 | 0.5 | _ | _ | _ | _ | _ | BARG
45 | PCV-2206C | PRESSURE REGULATOR |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 2.2 / 5 | 2 | _ | _ | _ | _ | _ | BARG
46 | PCV-2201C | PRESSURE REGULATOR |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 6/10 | 6 | _ | _ | _ | _ | _ | BARG
47 | PSV-2132C | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
48 | PSV-2133C | SAFETY VALVE |  |  | ON DISCHARGE LINE SNUBBER 2ND STAGE |  | BK-GCS-HY-120-PR-PI-0001 1C |  | 54.9 / 62 | 62 | _ | _ | _ | _ | _ | BARG
49 | RV-2200C | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
50 | RV-2201C | RELIFE VALVE |  |  | ON LUBE OIL |  | BK-GCS-HY-120-PR-PI-0001 5C |  | 6/10 | 7 | _ | _ | _ | _ | _ | BARG
51 | PSV-2203C | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG
52 | PSV-2204C | SAFETY VALVE |  |  | N2 TO CYLINDER PACKING INLET |  | BK-GCS-HY-120-PR-PI-0001 4C |  | 1 / 5 | 2.8 | _ | _ | _ | _ | _ | BARG