## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-EL-DS-0001
Document Title:D/SH (W/CURVE, DRAWING & CERTIFICATE) FOR COMPRESSOR MAIN MOTOR |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-SVTR-HY-0054 |  |  | Transmital Date:2024/05/12
[5 empty] | CRS No: NISOC-CRS- BK-GCS-HY-120-EL-DS-0001_V02 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 02/2294/507401 | 1402/12/08 | 1- ارسال نسخه AFC مطابق با توافقات صورتجلسه مورخ 1402/09/08 بوده، علی ایحال نقطه نظرات کارفرمای محترم به نحو مقتضی اعمال و مدرک مجددا با وشعیت AFC ارائه میگردد. 2- ملاحظه شد. 3- ملاحظه شد. 4- اطلاعات به همراه مهر سازنده در فاینال بوک ارائه خواهد شد. هر گونه انحراف پیش از ساخت اطلاع رسانی می گردد. 5- مورد تأیید است.
2 |  |  | 02/2294/507401 | 1402/12/08 | 1- پیش تر محاسبات shaft power ارائه و توسط کارفرمای اصلی محترم تایید شده است. 2- کلاس D اضافه شد. 3- به شماره گواهی درج شده در مدرک از طریق مدیر پروژهشرکت هوایار خدمتتان تقدیم خواهد گردید. شماره گواهی نامه ضد انفجار بر روی پلاک موتور و در دیتاشیت ارائه گردیده است. 4- اصلاح گردید. 5- سازنده استاندارد IEC 60034 را تأیید کرده است.
3 |  |  | 02/2294/507401 | 1402/12/08 | 5- سازنده استاندارد IEC 60034 را تأیید کرده است. 6- اصلاح گردید. 7- اصلاح گردید. 8- طبق فایل اولیه کارفرما محترم ارائه شده بود که اصلاح گردید. 9- اصلاح گردید. 10- نوع یاتاقان های استفاده شده در الکتروموتور به صورت hydrodynamic می باشد؛ که درون housing جدا از الکتروموتور تعبیه شده است و به صورت horizontal split (دارای دو کف بالا و پایین) است که دسترسی به بیرینگها برای چک، تعویض و اندازه گیری به راحتی ایجاد می شود.
4 |  |  | 02/2294/507401 | 1402/12/08 | 11- مورد تأیید است. 12- منظور TBD: to be determined بود که در رویژن جدید مقدارش درج گردید. 13- در P&ID صفحه oil-skid نمایش داده شده است. 14- بر اساس اعلام سازنده امکان پذیر نمی باشد. 15- ملاحظه گردید. 16- برند بیرینگها در دیتا شیت درج گردیده است. 17- ملاحظه شد.
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: