## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-IN-LI-0001 |  |  |  |  | Vendor Tr. N0: |  |  | Transmital Date:
Document Title: CAUSE & EFFECT CHARTS LIST |  |  |  |  | PEDCO Tr. No: BK-HD-PEDCO-SVTR-HY-0030 |  |  | Transmital Date: 2024/05/26
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-IN-LI-0001-V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بررسی وضعیت Lub Oil Cooler و Heater سیستم Lubricator در شرایط Start / Stop و Emergency Shutdown اضافه گردد. آیا دو تجهیز مذکور در شرایط Normal Operation بصورت دائم در سرویس می باشند؟ درخصوص Heater سیستم روغن Lubricator آیا نیاز به سیستم کنترل دمایی نمی باشد تا درصورت بالارفتن دما این Heater خاموش گردد؟ |  | BK-SUR-ENG-MEC-02-08614 | 2023-10-17 | Cooler به صورت Manual روشن و خاموش می شود. پس از Shutdown نیز به صورت Manual این تجهیز Stop می شود. Heater سیستم Lubricator دارای ترموستات داخلی بوده و اینترلاک برای آن تعریف نمی شود. این تجهیزات به صورت داءم در سرویس بوده که در رابطه با Lubricator Heater توضیحات داده شد.
2 | آیا منظور از note-3 این است که امکان compressor start از UCP وجود دارد؟ |  | BK-SUR-ENG-MEC-02-08614 | 2023-10-17 | مدارک بر اساس PID رویژن 4 اصلاح شد. همچنین PID رویژن 4 بر اساس صورتجلسه HAZOP اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Maleki Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 17 Oct 2023 |  |  |  |  | Date: