## Cover
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [8 empty] | شماره صفحه: 1 از 39
[5 empty] | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه
[5 empty] | BK | GCS | HY |  | 120 | IN | DS | 0001 | V03
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT DATASHEETS / CERTIFICATES نگهداشت و افزایش تولید میدان نفتی بینک
V03 | Jun.2024 |  |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  |  |  | M.SADEGHIAN
V02 | Dec..2023 |  |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  |  |  | S.Faramarzpour
V01 | Nov.2023 |  |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  |  |  | S.Faramarzpour
V00 | SEP.2023 |  |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  |  |  | M.Mehrshad
Rev. | Date |  |  | Purpose of Issue/Status |  |  |  | Prepared By |  |  | Checked By |  |  |  | Approved By | Client Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR:Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Rev.
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 2 از 39
[5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | HY | 120 | IN | DS |  | 0001 |  | V03
Tabulation Of Revised Pages
| Page | V00 | V01 | V02 |  | V03 |  | V04 |  |  | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | X | X | X |  | X |  |  |  |  | 1
| 2 | X | X | X |  | X |  |  |  |  | 2
| 3 | X | X | X |  | X |  |  |  |  | 3
| 4 | X | X | X |  | X |  |  |  |  | 4
| 5 | X | X | X |  | X |  |  |  |  | 5
| 6 | X | X | X |  | X |  |  |  |  | 6
| 7 | X | X | X |  | X |  |  |  |  | 7
| 8 | X | X | X |  | X |  |  |  |  | 8
| 9 | X | X | X |  | X |  |  |  |  | 9
| 10 | X | X | X |  | X |  |  |  |  | 10
| 11 | X | X | X |  | X |  |  |  |  | 11
| 12 | X | X | X |  | X |  |  |  |  | 12
| 13 | X | X | X |  | X |  |  |  |  | 13
| 14 | X | X | X |  | X |  |  |  |  | 14
| 15 | X | X | X |  | X |  |  |  |  | 15
| 16 | X | X | X |  | X |  |  |  |  | 16
| 17 | X | X | X |  | X |  |  |  |  | 17
| 18 | X | X | X |  | X |  |  |  |  | 18
| 19 | X | X | X |  | X |  |  |  |  | 19
| 20 | X | X | X |  | X |  |  |  |  | 20
| 21 | X | X | X |  | X |  |  |  |  | 21
| 22 | X | X | X |  | X |  |  |  |  | 22
| 23 | X | X | X |  | X |  |  |  |  | 23
| 24 | X | X | X |  | X |  |  |  |  | 24
| 25 | X | X | X |  | X |  |  |  |  | 25
| 26 | X | X | X |  | X |  |  |  |  | 26
| 27 | X | X | X |  | X |  |  |  |  | 27
| 28 | X | X | X |  | X |  |  |  |  | 28
| 29 | X | X | X |  | X |  |  |  |  | 29
| 30 | X | X | X |  | X |  |  |  |  | 30
| 31 | X | X | X |  | X |  |  |  |  | 31
| 32 | X | X | X |  | X |  |  |  |  | 32
| 33 | X | X | X |  | X |  |  |  |  | 33
| 34 | X | X | X |  | X |  |  |  |  | 34
| 35 | X | X | X |  | X |  |  |  |  | 35
| 36 | X | X | X |  | X |  |  |  |  | 36
| 37 | X | X | X |  | X |  |  |  |  | 37
| 38 | X | X | X |  | X |  |  |  |  | 38
| 39 | X | X | X |  | X |  |  |  |  | 39
| 40 | X | X | X | [6 empty] | 40
| 41 | X | X | X | [6 empty] | 41
| 42 |  |  | X | [6 empty] | 42
| 43 | [9 empty] | 43
| 44 | [9 empty] | 44

## Content
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [10 empty] | شماره صفحه: 3 از 39
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
|  |  | BK |  | GCS | HY | 120 | IN | DS |  | 0001 |  | V03
Table of Content
| Page | Content | [5 empty] | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | Cover | [5 empty] | 1
| 2 | Revised Pages | [5 empty] | 2
| 3 | Table of Content | [5 empty] | 3
| 4 | Pressure Gauge | [5 empty] | 4
| 5 | Pressure trasmitter data sheet | [5 empty] | 5
| 6 | Pressure trasmitter List | [5 empty] | 6
| 7 | Tempearture Gauge | [5 empty] | 7
| 8 | Tempearture Trasmitter data sheet | [5 empty] | 8
| 9 | Tempearture Trasmitter List | [5 empty] | 9
| 10 | Diff Pressure trasmitter data sheet | [5 empty] | 10
| 11 | Diff Pressure trasmitter List | [5 empty] | 11
| 12 | Diff Pressure Gauge data sheet | [5 empty] | 12
| 13 | Flow indicator Comp C-2101A | [5 empty] | 13
| 14 | Flow indicator Comp C-2101B | [5 empty] | 14
| 15 | Flow indicator Comp C-2101C | [5 empty] | 15
| 16 | Sight Glass data sheet | [5 empty] | 16
| 17 | Sight Glass data List | [5 empty] | 17
| 18 | Flow transmitter 2121A | [5 empty] | 18
| 19 | Flow transmitter 2131A | [5 empty] | 19
| 20 | Flow transmitter C-2206A | [5 empty] | 20
| 21 | Flow transmitter 2121B | [5 empty] | 21
| 22 | Flow transmitter 2131B | [5 empty] | 22
| 23 | Flow transmitter C-2206B | [5 empty] | 23
| 24 | Flow transmitter 2121C | [5 empty] | 24
| 25 | Flow transmitter 2131C | [5 empty] | 25
| 26 | Flow transmitter C-2206C | [5 empty] | 26
| 27 | Level gauge C-LG-2213A | [5 empty] | 27
| 28 | Level gauge C-LG-2213B | [5 empty] | 28
| 29 | Level gauge C-LG-2213C | [5 empty] | 29
| 30 | Level Transmitter C-LT-2213A | [5 empty] | 30
| 31 | Level Transmitter C-LT-2213B | [5 empty] | 31
| 32 | Level Transmitter C-LT-2213C | [5 empty] | 32
| 33 | Solenoid Data sheet | [5 empty] | 33
| 34 | Solenoid List | [5 empty] | 34
| 35 | Level Transmitter C-LT-2200A | [5 empty] | 35
| 36 | Level Transmitter C-LT-2200B | [5 empty] | 36
| 37 | Level Transmitter C-LT-2200C | [5 empty] | 37
| 38 | Pressure switch data Sheet | [5 empty] | 38
| 39 | Temp switch data Sheet | [5 empty] | 39
| 40 | [6 empty] | 40
| 41 | [6 empty] | 41

## PG
NISOC | [8 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 | [8 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [20 empty] | شماره صفحه: 4 از 39
[9 empty] | پروژه |  |  |  | بسته کاری |  | صادرکننده | تسهیلات |  |  | رشته |  |  | نوع مدرک |  |  |  | سریال |  |  | نسخه
[9 empty] | BK |  |  |  | GCS |  | HY | 120 |  |  | IN |  |  | DS |  |  |  | 0001 |  |  | V03
Data Sheet for Pressure Gauge
1 | Type : | Direct Rdg. | [5 empty] | 3-15 lb Reciever | [7 empty] | 11 | MFR.& Model No. | [6 empty] | Wika 233.30.160
|  | Other | liquid filled | [12 empty] | 12 | Press Element : Bourdon | [10 empty] | Bellows
2 | Mounting : | Surface |  |  | Local | [5 empty] | Flush | [11 empty] | Other
3 | Dial : | Diameter |  | 160 mm |  |  | Color : White / Black Lettering ,Aluminum Non Rusting Metal | [8 empty] | 13 | Element Mtl. : | [5 empty] | Bronze |  |  |  | Steel
4 | Case : | Cast Iron |  |  |  |  | S.S |  |  |  |  | Phenol | [7 empty] | SS |  |  | Other |  | 316SS
|  | Other | [13 empty] | 14 | Socket Mtl. : | [5 empty] | Bronze |  |  |  | Steel
5 | Ring : | Screwed |  |  | Hinged | [6 empty] | Slip | [7 empty] | SS |  |  | Other |  | 316SS
|  | Std |  |  | Other | [10 empty] | 15 | Connection-NPT : | [5 empty] | 1/4 in. |  |  |  | 1/2 in. |  |  |  | Other | NPTM (refer to note)
6 | Blow-out Protection : |  |  |  | None |  |  |  |  | Back |  |  | Disc | [9 empty] | Bottom |  |  |  | Back
|  | Solid Front | [6 empty] | Other | [6 empty] | 16 | Movement: | [5 empty] | Bronze |  |  |  | SS
7 | Lens : | Glass |  |  | Plastic |  |  |  | Safety Glass ( shatter proof) | [11 empty] | Naylon |  |  |  |  | Other |  |  |  | Stainless Steel
8 | Options : | [14 empty] | 17 | Diaphragm Seal |  |  |  | As per List
[10 empty] | As per List | [8 empty] | MFR. | [9 empty] | Type
[19 empty] | Wetted Part Mtl. | [9 empty] | Other Mtl.
Fill Fluid :
9 | Nominal Accuracy Required : |  |  |  |  | ± 1% of full scale | [12 empty] | Process Conn. :
10 | Over range protection : |  |  | 1.3 times the maximum scale reading | [11 empty] | 18 | Ingress Protection : | [5 empty] | IP 65
[16 empty] | 19 | Manifold S.S316 2 valve
Item | Tag No. |  | Range (barg) |  |  |  | Process Fluid/State | Design | [5 empty] | Operating |  |  |  | LINE NO./EQUIPMENTNO. | [7 empty] | P&ID NO. | [6 empty] | Accessories | NOTE
[8 empty] | Press (barg) |  |  |  | Temp (C°) |  | Press (barg) |  | Temp (C°) Summer /Winter
1 | C-PG-2190A |  | 0-10 |  |  |  | Process gas Comp A | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 / 18.9 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1A | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 10 barg
2 | C-PG-2191A |  | 0-40 |  |  |  | Process gas Comp A | 24.5 |  |  |  | 180 |  | 18 |  | 129/116 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1A | [6 empty] | Cooling Element Nace material
3 | C-PG-2193A |  | 0-40 |  |  |  | Process gas Comp A | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1A | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 40 barg
4 | C-PG-2194A |  | 0-100 |  |  |  | Process gas Comp A | 62 |  |  |  | 180 |  | 54.9 |  | 148/149 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1A | [6 empty] | Cooling Element Nace material
5 | C-PG-2200A |  | 0-16 |  |  |  | Instrument Air Comp A | 12.5 |  |  |  | 85 |  | 6 |  | 65 |  | ISA-112-0002A-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2A
6 | C-PG-2201A |  | 0-10 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0004A-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3A
7 | C-PG-2202A |  | 0-10 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0003A-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3A
8 | C-PG-2204A |  | 0-10 |  |  |  | Lube Oil Comp A | 10 |  |  |  | 85 |  | 5 |  | 60 |  | OIL-112-0008A-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3A
9 | C-PG-2205A |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009A-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1A | [6 empty] | Nace material
10 | C-PG-2206A |  | 0-10 |  |  |  | Water console Comp A | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0003A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5A | [6 empty] | Pulsation Damper (Snubber)
11 | C-PG-2207A |  | 0-10 |  |  |  | Water console Comp A | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0004A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5A | [6 empty] | Pulsation Damper (Snubber)
12 | C-PG-2208A |  | 0-10 |  |  |  | Water console Comp A | 8 |  |  |  | 85 |  | 3 |  | 63 |  | CWS-112-0002A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5A
13 | C-PG-2190B |  | 0-10 |  |  |  | Process gas Comp B | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 / 18.9 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1B | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 10 barg
14 | C-PG-2191B |  | 0-40 |  |  |  | Process gas Comp B | 24.5 |  |  |  | 180 |  | 18 |  | 129/116 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1B | [6 empty] | Cooling Element Nace material
15 | C-PG-2193B |  | 0-40 |  |  |  | Process gas Comp B | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1B | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 40 barg
16 | C-PG-2194B |  | 0-100 |  |  |  | Process gas Comp B | 62 |  |  |  | 180 |  | 54.9 |  | 148/149 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1B | [6 empty] | Cooling Element Nace material
17 | C-PG-2200B |  | 0-16 |  |  |  | Instrument Air Comp B | 12.5 |  |  |  | 85 |  | 6 |  | 65 |  | ISA-112-0002B-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2B
18 | C-PG-2201B |  | 0-10 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0004B-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3B
19 | C-PG-2202B |  | 0-10 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0003B-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3B
20 | C-PG-2204B |  | 0-10 |  |  |  | Lube Oil Comp B | 10 |  |  |  | 85 |  | 5 |  | 60 |  | OIL-112-0008B-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3B
21 | C-PG-2205B |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009B-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1B | [6 empty] | Nace material
22 | C-PG-2206B |  | 0-10 |  |  |  | Water console Comp B | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0003B-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5B | [6 empty] | Pulsation Damper (Snubber)
23 | C-PG-2207B |  | 0-10 |  |  |  | Water console Comp B | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0004B-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5B | [6 empty] | Pulsation Damper (Snubber)
24 | C-PG-2208B |  | 0-10 |  |  |  | Water console Comp B | 8 |  |  |  | 85 |  | 3 |  | 63 |  | CWS-112-0002A-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5B
25 | C-PG-2190C |  | 0-10 |  |  |  | Process gas Comp C | 24.5 |  |  |  | 180 |  | 4.9 |  | 36.8 / 18.9 |  | 1ST STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1C | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 10 barg
26 | C-PG-2191C |  | 0-40 |  |  |  | Process gas Comp C | 24.5 |  |  |  | 180 |  | 18 |  | 129/116 |  | 1ST STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1C | [6 empty] | Cooling Element Nace material
27 | C-PG-2193C |  | 0-40 |  |  |  | Process gas Comp C | 62 |  |  |  | 180 |  | 17.1 |  | 59.9 |  | 2nd STAGE SUCTION SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1C | [6 empty] | Cooling Element Nace material Over Pressure Protector Set point 40 barg
28 | C-PG-2194C |  | 0-100 |  |  |  | Process gas Comp C | 62 |  |  |  | 180 |  | 54.9 |  | 148/149 |  | 2nd STAGE DISCHARGE SNUBBER | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1C | [6 empty] | Cooling Element Nace material
29 | C-PG-2200C |  | 0-16 |  |  |  | Instrument Air Comp C | 12.5 |  |  |  | 85 |  | 6 |  | 65 |  | ISA-112-0002C-AZ00-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page2C
30 | C-PG-2201C |  | 0-10 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0004C-S.S-1.1/2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3C
31 | C-PG-2202C |  | 0-10 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 5 |  | 70 |  | OIL-112-0003C-S.S-2"-NP | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3C
32 | C-PG-2204C |  | 0-10 |  |  |  | Lube Oil Comp C | 10 |  |  |  | 85 |  | 5 |  | 60 |  | OIL-112-0008C-S.S-2"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page3C
33 | C-PG-2205C |  | 0-6 |  |  |  | GAS | 5 |  |  |  | 85 |  | 1.5 |  | 65 |  | FLR-112-0009C-AN07-1"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page1C | [6 empty] | Nace material
34 | C-PG-2206C |  | 0-10 |  |  |  | Water console Comp C | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0003C-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5C | [6 empty] | Pulsation Damper (Snubber)
35 | C-PG-2207C |  | 0-10 |  |  |  | Water console Comp C | 8 |  |  |  | 85 |  | 4 |  | 70 |  | CWS-112-0004C-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5C | [6 empty] | Pulsation Damper (Snubber)
36 | C-PG-2208C |  | 0-10 |  |  |  | Water console Comp C | 8 |  |  |  | 85 |  | 3 |  | 63 |  | CWS-112-0002C-C.S-3"-IS | [7 empty] | BK-GCS-HY-120-PR-PI-0001 Page5C

## PT
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 5 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V03
Data Sheet for Pressure Transmitter
| 1 | Tag No.: (Refer to Next Page) | Service: (Refer to Next Page)
GENERAL | 2 | Function | Recordo Indicaten Controlo Blindo Transn Intego (Note1)
| 3 | Case | MFR STDn Nom Sizeo Color MFR STDn Other
| 4 | Mounting | Flusho Surfaceo Yoken Other
| 5 | Enclosure Class | General Purposeo Weather Proof n Explosion-Proof o Class
|  |  | For use in Intrinsically Safe Systemn | [5 empty] | Other EExia, IIB, T4
| 6 |  | Ingress Protection : IP 66
| 7 | Power Supply | 117 V 60 Hzo Other: aco dcn Volts : 24 VDC Loop Powered
TRANSMITTER | 8 | Trans. Output | 4-20mAn 10-50mAo 21-10 kpa(3-15 psig)o Other 4-20mA Smart HART
| 9 |  | Transmitter Accuracy : 0.1% of full scale.
UNIT | 10 | Service | Gage Press n Vacuumo Absoluteo Compound o
| 11 | Element Type | Diaphragmn Helixo Bourdon o Bellowso Fill Fluid:Silicone
| 12 | Material | Body Aluminum Element 316 S.S. as minimum
| 13 | Range | Fixedo Adj. Range n Set At (Refer to Next Page)
| 14 | Rating | Overrange Protection: at least 1.5 times the maximum range
| 15 | Process Data | Press: Normal Max Element Range (Refer to Next Page)
| 16 | Process Conn. | ½ in. NPTn Other Male with wrench flats
| 17 |  | Location: Bottom n Back o Other
| 18 | Electrical Conn. | MFR STDo Other ISO M20x1.5
OPTIONS | 19 | Miscellaneous | Filt Reg.o Sup. Gageo Output Gageo Charts
| 20 | Diaphragm Seal | Diaph Seal o Type : Capillary Length: Mtl. :
Conn. Fill Fluid : shall be Suitable for Normal and Max. Operating Temp
Flushing Connection :
| 21 | Manifold | Valve Manifold : See list
| 22 | MFR. & Model No. | See PT list
Notes:
1- All transmitters shall be provided complete with LCD type integral indicator .
2- Repeatability of the transmitter shall be better than 0.1% of the span.
3- All transmitters shall be reverse polarity protected.
4- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
5- NACE MR-01-75 to be considered.

## PT List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 39
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V03
List of PT
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | VISCOSITY (cP) | CALIBRATED RANGE (Barg) | ACCESSORIES Option | MFR. & Model No. | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Norm. / Design | VISCOSITY (Cst) |  | ACCESSORIES | ACCESSORIES | REV. Remark
1 | PT-2123A | Process gas Comp A | GAS-111-0031A-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1A | 1" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.0115 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
2 | C-PT-2133A | Process gas Comp A | GAS-111-0051A-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1A | 1" NPT | Gas | 54.9 / 62 | 148 / 180 | 0.0164 | 0-65 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG4A2B21BB4I1
3 | PT-2124A | Process gas Comp A | GAS-111-0036A-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1A | 1" NPT | Gas | 18 / 22 | 129 / 180 | 0.0149 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
4 | PT-2132A | Process gas Comp A | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1A | 1/2" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.0126 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
5 | C-PT-2201A | Instrument Air Comp A | ISA-112-0002A-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2A | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1
6 | C-PT-2200A | Lubricator Comp A | OIL-112-0008A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3A | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
7 | C-PT-2204A | Lube Oil Comp A | OIL-112-0008A-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3A | 1" NPT | Liquid | 5 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
8 | C-PT-2210A | N2 Gas Supply Comp A | NIT-112-0001A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4A | 1" NPT | Gas | 2 / 5 | 60 / 85 | 0.0199 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
9 | C-PT-2211A | N2 Gas Supply Comp A | NIT-112-0002A-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4A | 1" NPT | Gas | 0.5 / 5 | 60 / 85 | 0.0199 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
9 | C-PT-2212A | N2 Gas | FLR-112-0012A-AN07-1.1/2"-IS | BK-GCS-HY-120-PR-PI-0001-Page4A | 1" NPT | Gas | 1 / 5 | 60 / 85 | 0.0198 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
10 | C-PT-2220A | Water console Comp A | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5A | 1" NPT | Liquid | 3 / 10 | 63 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
11 | C-PT-2221A | Water console Comp A | CWS-112-0002A-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5A | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316
12 | PT-2123B | Process gas Comp B | GAS-111-0031B-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1B | 1" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.0115 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
13 | C-PT-2133B | Process gas Comp B | GAS-111-0051B-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1B | 1" NPT | Gas | 54.9 / 62 | 148 / 180 | 0.0164 | 0-65 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG4A2B21BB4I1
14 | PT-2124B | Process gas Comp B | GAS-111-0036B-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1B | 1" NPT | Gas | 18 / 22 | 129 / 180 | 0.0149 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
15 | PT-2132B | Process gas Comp B | GAS-111-0044B-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1B | 1" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.0126 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
16 | C-PT-2201B | Instrument Air Comp B | ISA-112-0002B-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2B | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1
17 | C-PT-2200B | Lubricator Comp B | OIL-112-0008B-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3B | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
18 | C-PT-2204B | Lube Oil Comp B | OIL-112-0008B-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3B | 1" NPT | Liquid | 5 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
19 | C-PT-2210B | N2 Gas Supply Comp B | NIT-112-0001B-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4B | 1" NPT | Gas | 2 / 5 | 60 / 85 | 0.0199 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
20 | C-PT-2211B | N2 Gas Supply Comp B | NIT-112-0002B-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4B | 1" NPT | Gas | 0.5 / 5 | 60 / 85 | 0.0198 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
9 | C-PT-2212B | N2 Gas | FLR-112-0012A-AN07-1.1/2"-IS | BK-GCS-HY-120-PR-PI-0001-Page4B | 1" NPT | Gas | 1 / 5 | 60 / 85 | 0.0198 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
21 | C-PT-2220B | Water console Comp B | CWS-112-0002B-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5B | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
22 | C-PT-2221B | Water console Comp B | CWS-112-0002B-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5B | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316
23 | PT-2123C | Process gas Comp C | GAS-111-0031C-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1C | 1" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.0115 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
24 | C-PT-2133C | Process gas Comp C | GAS-111-0051C-FN05-6"-IS | BK-GCS-HY-120-PR-PI-0001-Page1C | 1" NPT | Gas | 54.9 / 62 | 148 / 180 | 0.0164 | 0-65 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG4A2B21BB4I1
25 | PT-2124C | Process gas Comp C | GAS-111-0036C-CN05-6"-PT | BK-GCS-HY-120-PR-PI-0001-Page1C | 1" NPT | Gas | 18 / 22 | 129 / 180 | 0.0149 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
26 | PT-2132 | Process gas Comp C | GAS-111-0044C-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1C | 1" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.0126 | 0-25 | Wetted Part S.S316 Nace 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1 | Loose Item
27 | C-PT-2201C | Instrument Air Comp C | ISA-112-0002C-AZ00-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page2C | 1" NPT | Gas | 6 / 12.5 | 65 / 85 | 0.021 | 0-16 | 2 valve manifold S.S316 | Rosemount 3051TG3A2B21BB4I1
28 | C-PT-2200C | Lubricator Comp C | OIL-112-0008C-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3C | 1/2" NPT | Liquid | 6 / 10 | 65 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
29 | C-PT-2204C | Lube Oil Comp C | OIL-112-0008C-S.S-2"-IS | BK-GCS-HY-120-PR-PI-0001-Page3C | 1" NPT | Liquid | 5 / 10 | 60 / 85 | 40 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
30 | C-PT-2210C | N2 Gas Supply Comp C | NIT-112-0001C-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4C | 1" NPT | Gas | 2 / 5 | 60 / 85 | 0.0199 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
31 | C-PT-2211C | N2 Gas Supply Comp C | NIT-112-0002C-SS-1"-NP | BK-GCS-HY-120-PR-PI-0001-Page4C | 1" NPT | Gas | 0.5 / 5 | 60 / 85 | 0.0198 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
9 | C-PT-2212C | N2 Gas | FLR-112-0012A-AN07-1.1/2"-IS | BK-GCS-HY-120-PR-PI-0001-Page4C | 1" NPT | Gas | 1 / 5 | 60 / 85 | 0.0198 | 0-6 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
32 | C-PT-2220C | Water console Comp C | CWS-112-0002C-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5C | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316 | Rosemount 3051TG2A2B21BB4I1
33 | C-PT-2221C | Water console Comp C | CWS-112-0002C-C.S-3"-IS | BK-GCS-HY-120-PR-PI-0001-Page5C | 1" NPT | Liquid | 3 / 10 | 58 / 85 | 0.478 | 0-10 | 2 valve manifold S.S316

## TEMPERATURE GAUGE(BIMETAL)
NISOC |  |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | پروژه |  |  | بسته کاری |  | صادر کننده |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 7 از 39
[5 empty] | BK |  |  | GCS |  | HY |  | 120 |  |  | IN | DS |  | 0001 |  | V03
BI-METALLIC THERMOMETER WITH WELL (Complete Assembly)
| THERMOMETER | [15 empty] | WELL
1 | ELEMENT TYPE |  | BI-METAL ■ |  |  |  |  | GAS FILLED CAPILLARY □ | [7 empty] | 15 | NONE □ |  |  |  |  | INCLUDED ■
2 | STEM | THREADED (NPTM) ■ |  |  |  | UNION □ |  |  |  |  | PLAIN □ |  |  |  |  | 16 | MATERIAL : |  |  |  | 304 SS □ |  | 316 SS ■ |  | OTHER
| MATERIAL |  | S.S | [12 empty] | 17 | CONSTRUCTION |  |  |  |  | BUILT-UP □ |  | DRILLED BAR STOCK ■
3 | STEM OR UNION THREADED : | [5 empty] | 1/2 IN. ■ |  |  |  | 3/4 IN. □ | [10 empty] | OTHER
4 | STEM DIAMETER |  |  |  | MFR. STD □ |  |  | 6 mm. ■ | [5 empty] | 8 mm. □ | [7 empty] | TAPERED ■ |  | STRAIGHT □
5 | CASE MATERIAL : |  |  |  | MFR. STD □ |  |  |  | OTHER |  | S.S |  |  |  |  | 18 | INTERNAL CONNECTION NOMINAL SIZE | [6 empty] | 1/2" PIPE THREAD
6 | DIAL : | SIZE |  | 160 mm |  |  |  | COLOR |  | White / Black Lettering Aluminum,Non Rusting Metal | [5 empty] | 19
7 | SCALE TYPE : |  | °C |  |  |  | POINTER ADJUSTMENT | [6 empty] | YES |  | 20
8 | SCALE LENGTH : |  |  | MFR. STD. |  |  |  | COLOR |  | MFR.STD | [5 empty] | 21
9 | FORM : |  | FIG NO. |  | EVERY ANGLE | [10 empty] | 22 | FLANGE RATING |  |  |  | REFER TO BELOW TABLE
10 | EXTERNAL CALIBRATOR ■ | [6 empty] | `
11 | PROTECTION CLASS : |  |  |  | IP65 | [10 empty] | 23 | MANUFACTURER |  |  |  | Wika
12 | ACCURACY : |  |  |  | ±1 % OF FULL SCALE RANGE | [10 empty] | 24 | MODEL NO. |  |  |  | S5551
13 | WINDOW MATERIAL : |  | SHATTER PROOF TYPE
14 | RING TYPE/MATERIAL : |  |  |  | SCREWED/S.S316
ITEM NO. | TAG NO. | LINE SIZE | WELL "U" mm (*) (NOTE 1) |  |  | STEM LENGTH (mm) (*) |  | OPER. TEMP. (°C) |  | DESIGN TEMP.(°C)/ PRESSURE (BARG) |  | Density (kg/m3) | RANGE (°C) |  | PRESSURE (barg) Norm./ Max. | PROCESS/WELL CONNECTION & RATING (ANSI) |  |  | Max. VELOCITY (cP) |  |  | SERVICE |  |  | P&ID NO. | NOTES
1 | C-TG-2190A | 1ST STAGE SUCTION SNUBBER SCH 80 | 500 |  |  | 540 |  | 36.8 |  | 180 / 24.5 |  | 5.77 | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1A | Thermowell S.S316 Nace
2 | C-TG-2193A | 2nd STAGE SUCTION SNUBBER SCH 160 | 500 |  |  | 540 |  | 59.9 |  | 180 / 62 |  | 17.1 | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1A | Thermowell S.S316 Nace
3 | C-TG-2204A | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3A
4 | C-TG-2205A | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3A
5 | C-TG-2206A | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 70 |  | 85 / 10 |  | 862 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3A
6 | C-TG-2210A | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page4A | Thermowell S.S316 Nace
7 | C-TG-2211A | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page4A | Thermowell S.S316 Nace
8 | C-TG-2217A | Water Reservoir | 400 |  |  | 450 |  | 65 |  | 85 / 3.5 |  | 1059 | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5A
9 | C-TG-2221A | 3" TO 4" (Expanded) SCH 40 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1059 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5A
10 | C-TG-2215A | 1" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6A
11 | C-TG-2216A | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6A
12 | C-TG-2212A | 3" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 58 |  | 85 / 7 |  | 1065 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5A
13 | C-TG-2213A | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6A
14 | C-TG-2214A | 2'1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6A
15 | C-TG-2190B | 1ST STAGE SUCTION SNUBBER SCH 80 | 500 |  |  | 540 |  | 36.8 |  | 180 / 24.5 |  | 5.77 | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1B | Thermowell S.S316 Nace
16 | C-TG-2193B | 2nd STAGE SUCTION SNUBBER SCH 160 | 500 |  |  | 540 |  | 59.9 |  | 180 / 62 |  | 17.1 | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1B | Thermowell S.S316 Nace
17 | C-TG-2204B | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3B
18 | C-TG-2205B | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3B
19 | C-TG-2206B | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 70 |  | 85 / 10 |  | 862 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3B
20 | C-TG-2210B | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page4B | Thermowell S.S316 Nace
21 | C-TG-2211B | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page4B | Thermowell S.S316 Nace
22 | C-TG-2217B | Water Reservoir | 400 |  |  | 450 |  | 65 |  | 85 / 3.5 |  | 1059 | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5B
23 | C-TG-2221B | 3" TO 4" (Expanded) SCH 40 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1059 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5B
24 | C-TG-2215B | 1" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6B
25 | C-TG-2216B | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6B
26 | C-TG-2212B | 3" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 58 |  | 85 / 7 |  | 1065 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5B
27 | C-TG-2213B | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6B
28 | C-TG-2214B | 2'1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6B
29 | C-TG-2190C | 1ST STAGE SUCTION SNUBBER SCH 80 | 500 |  |  | 540 |  | 36.8 |  | 180 / 24.5 |  | 5.77 | 0-200 |  | 4.9 / 22 | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1C | Thermowell S.S316 Nace
30 | C-TG-2193C | 2nd STAGE SUCTION SNUBBER SCH 160 | 500 |  |  | 540 |  | 59.9 |  | 180 / 62 |  | 17.1 | 0-200 |  | 17.1 / 22 | 2" #600 1/2" NPT Back |  |  | 40 |  |  | Process Gas Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1C | Thermowell S.S316 Nace
31 | C-TG-2204C | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3C
32 | C-TG-2205C | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 60 |  | 85 / 10 |  | 870 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3C
33 | C-TG-2206C | 2" TO 4" (Expanded) SCH 10 | 200 |  |  | 200 |  | 70 |  | 85 / 10 |  | 862 | 0-120 |  | 5 / 6 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Lube Oil Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3C
34 | C-TG-2210C | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page4C | Thermowell S.S316 Nace
35 | C-TG-2211C | 2" TO 4" (Expanded) SCH XXS | 200 |  |  | 200 |  | 60 |  | 85 / 5 |  | 2.5 | 0-120 |  | 2 / 2.2 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | N2 Gas Supply Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page4C | Thermowell S.S316 Nace
36 | C-TG-2217C | Water Reservoir | 400 |  |  | 450 |  | 65 |  | 85 / 3.5 |  | 1059 | 0-120 |  | ATM / ATM | 2" #300 1/2" NPT Back |  |  | 40 |  |  | Water console Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5C
37 | C-TG-2221C | 3" TO 4" (Expanded) SCH 40 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1059 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5C
38 | C-TG-2215C | 1" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6C
39 | C-TG-2216C | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6C
40 | C-TG-2212C | 3" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 58 |  | 85 / 7 |  | 1065 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Water console |  |  | BK-GCS-HY-120-PR-PI-0001-Page5C
41 | C-TG-2213C | 1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6C
42 | C-TG-2214C | 2'1/2" TO 4" (Expanded) SCH 80 | 200 |  |  | 200 |  | 65 |  | 85 / 7 |  | 1060 | 0-120 |  | 3 / 4 | 1 1/2" #300 1/2" NPT |  |  | 40 |  |  | Jacket Cooling Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6C

## TT
NISOC |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
INSTRUMENT DATASHEETS / CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  |  | پروژه |  | بسته کاری |  | صادر کننده |  | تسهیلات |  | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 39
|  |  |  | BK |  | GCS |  | HY |  | 120 |  | IN | DS | 0001 |  | V03
Data Sheet for Temprarure Transmitter/Element/Thermowell
| HEAD | [12 empty] | 21 | BORE DIAMETER 6.6 mm (NOTE 4)
1 | COMPLETE ASSEMBLY |  |  |  | YES |  | OTHER | [6 empty] | 22 | OUTSIDE DIAMETER AT SUPPORT/TIP : 28/22 mm (NOTE 4)
2 | SCREWED COVER ■ |  |  |  |  | OTHER | [7 empty] | 23 | LAGGING EXTENTION "T" : VTA
3 | PROTECTION CLASS |  |  |  | IP-66 | [8 empty] | 24 | TEST : HYDROSTATIC AND PENETRANT TEST
4 | HAZ. AREA CLASSIFICATION |  |  |  | EXia IIB T4 | [8 empty] | 25 | CONNECTION TO SENSOR |  |  |  |  | 1/2" NPT F
5 | MATERIAL | 316 S.S |  |  | ELECTRICAL CONN. | [5 empty] | M20 X 1.5 |  |  | 26 | PROCESS CONNECTION |  |  |  | See list
6 | NIPPLE SIZE | 1/2" |  |  | DIM."N" | [5 empty] | UNION □
7 | AMBIENT TEMPERATURE IN DIRECT SUNLIGHT | [13 empty] | PERFORMANCE CHARACTERISTICS
| ELEMENT | [12 empty] | 27 | MIN/MAX. AMBIENT WORKING TEMPERATURE: | [6 empty] | BY VENDOR
8 | PLATINUM ■ 100/0°C |  | NICKEL □ |  |  |  |  | OTHER
9 | TYPE |  | PT100 | [11 empty] | TRANSMITTER
10 | TEMPERATURE RANGE |  |  | -100ºC to 500 ºC | [9 empty] | 28 | TRANSMITTER BODY MATERIAL |  |  |  |  | EXOPXY PAINTED DIE CAST ALUMINIUM
11 | LEADS | STD □ |  |  | POTTED □ |  |  |  |  | HERM. SEALED ■ |  |  |  | 29 | POWER SUPPLY | [5 empty] | 24 VDC, LOOP POWERED WITH HART
12 | SHEAT MATERIAL |  | 316 S.S. |  |  | O.D. |  |  |  | 6 mm |  |  |  | 30 | OUTPUT RANGE | [5 empty] | 4-20 ma
13 | TYPE | SINGLE ■ |  |  |  | DUPLEX □ | [7 empty] | 31 | TRANSMITTER MOUNTING | [5 empty] | HEAD MOUNTED
14 | SPRING LOADED |  |  | YES ■ |  |  | NO □ | [6 empty] | 32 | ELECTRICAL CONNECTION | [5 empty] | ISO M20
15 | CONNECTION | 2-WIRE □ |  |  | 3-WIRE ■ |  |  | 4-WIRE □ | [5 empty] | 33 | ACCURACY |  |  | ± 0.1 % OF CALIBRATED SPAN
16 | LEAD WIRES ■ |  | RECEPTACLE □ | [5 empty] | TERMINAL BLOCK ■ |  |  |  |  | 34 | ENCLOSURE APPROVAL | [5 empty] | ATEX
| OTHER | [12 empty] | 35 | ZERO ADJUST: YES SPAN ADJUST:YES
| WELL OR TUBE | [12 empty] | 36 | ISOLATION TYPE: Barier
17 | NONE □ INCLUDE ■ BY OTHERS □ | [12 empty] | 37 | NIPPLE & UNION MATERIAL: S.S
18 | MATERIAL |  | AISI 316 S.S. | [10 empty] | 38 | LCD INDICATOR: YES
19 | CONSTRUCTION |  | TAPERED ■ |  |  |  |  | STRAIGHT □ | [5 empty] | 39 | MANUFACTURER: * |  | See list |  |  | MODEL NO. : See list
20 | SOILD BAR-STOCK ■ |  |  | BUILT-UP □ |  |  |  | CLOSE-END TUBE □
NOTES :
* VENDOR TO CONFIRM
1) VENDOR SHALL FULLY SUPPLY & ASSEMBLE THERMOWELL WITH THERMOELEMENT AND HEAD MOUNTED TRANSMITTER.
2) SURFACE TEMPERATURE WILL REACH TO 85˚C IN EXPOSURE OF DIRECT SUNLIGHT.
3) HEAD COVER SHALL BE FRONT GLASS TYPE FOR COMPATIBILITY OF INDICATOR REQUIREMENT
4)WAKE FREQUENCY CALCULATION SHALL BE SUBMITTED BY MANUFACTURE FOR FINALIZING ALL THERMOWELL SIZE. (ASME PTC 19.3)
5)THE LINE SIZE SHALL BE EXPANDED TO 4".
6)REFER TO IPS-D-IN-101" FOR THERMOWELL DIMENSION.
7)COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## TT List
NISOC | [7 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
شماره پیمان: 9184 – 073 - 053 | [7 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 9 از 39
[8 empty] | پروژه |  | بسته کاری |  | صادر کننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه
[8 empty] | BK |  | GCS |  | HY | 120 | IN |  | DS | 0001 |  | V03
List of TT/TE/TW
ITEM NO. | TAG NO. | LINE SIZE | WELL DIMENTION (mm) (*) |  | Density (kg/m3) | OPER. TEMP. (°C) | DESIGN TEMP.(°C) |  | MAX VELOCITY (m/s) |  | RANGE (°C) | PRESSURE Nor./Des. (barg) | PROCESS CONNECTION & RATING (ANSI) |  | INDICATOR | TRANSMITTER MOUNTING |  | SERVICE |  |  | P&ID NO. | MFR. & Model No. | NOTES
|  |  | U | STEM
1 | TT-2122A | 8" SCH20 | 200 | 240 | 5.77 | 36.8 / 18.9 | 180 |  | 9 |  | 0-200 | 4.9 / 22 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0031A-CN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
2 | C-TT-2191A | _ | 500 | 540 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | Process Gas 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
3 | TT-2123A | 6"SCH20 | 200 | 240 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
4 | TT-2132A | 6" SCH20 | 200 | 240 | 17.1 | 59.9 | 180 |  | 8 |  | 0-200 | 17.1 / 22 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
5 | TT-2133A | 6" SCH20 | 200 | 240 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
6 | C-TT-2194A | _ | 500 | 540 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | Process Gas 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
7 | C-TT-2204A | 2" TO 4"SCH10 (Expanded) | 150 | 200 | 870 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
8 | C-TT-2203A | _ | 200 | 250 | 862 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase CompA |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
9 | C-TT-2213A | _ | 400 | 450 | 1059 | 70 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
10 | C-TT-2214A | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
11 | C-TT-2215A | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
12 | C-TT-2216A | Bare block | 2000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp DE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
13 | C-TT-2218A | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp NDE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
14 | C-TT-2217A | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
15 | C-TT-2219A | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
16 | C-TT-2220A | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Mid Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
17 | C-TT-2221A | 3" TO 4"SCH40 (Expanded) | 200 | 250 | 250 | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
18 | TE-2222A TE-2223A TE-2224A | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
19 | TE-2225A TE-2226A TE-2227A | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
20 | TE-2228A TE-2229A TE-2230A | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
21 | TT-2122B | 8" SCH20 | 200 | 240 | 5.77 | 36.8 / 18.9 | 180 |  | 9 |  | 0-200 | 4.9 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0031A-CN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
22 | C-TT-2191B | _ | 500 | 540 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
23 | TT-2123B | 6"SCH20 | 200 | 240 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
24 | TT-2132B | 6" SCH20 | 200 | 240 | 17.1 | 59.9 | 180 |  | 8 |  | 0-200 | 17.1 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
25 | TT-2123B | 6" SCH20 | 200 | 240 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | Direct Mounted |  | GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
26 | C-TT-2194B | _ | 500 | 540 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
27 | C-TT-2204B | 2" TO 4"SCH10 (Expanded) | 150 | 200 | 870 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
28 | C-TT-2203B | _ | 200 | 250 | 862 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase CompA |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
29 | C-TT-2213B | _ | 400 | 450 | 1059 | 70 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
30 | C-TT-2214B | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
31 | C-TT-2215B | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
32 | C-TT-2216B | Bare block | 2000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp DE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
33 | C-TT-2218B | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp NDE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
34 | C-TT-2217B | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
35 | C-TT-2219B | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
36 | C-TT-2220B | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Mid Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
37 | C-TT-2221B | 3" TO 4"SCH40 (Expanded) | 200 | 250 | 250 | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Cooling water header CWS-112-0002A-C.S-3"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
38 | TE-2222B TE-2223B TE-2224B | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 |  | RTD in main motor
39 | TE-2225B TE-2226B TE-2227B | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
40 | TE-2228B TE-2229B TE-2230B | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
41 | TT-2122C | 8" SCH20 | 200 | 240 | 5.77 | 36.8 / 18.9 | 180 |  | 9 |  | 0-200 | 4.9 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0031A-CN05-8"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
42 | C-TT-2191C | _ | 500 | 540 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 2", 300# |  | Yes | REMOTE TYPE |  | 1STG DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
43 | TT-2123C | 6"SCH20 | 200 | 240 | 14.42 | 129 / 116 | 180 |  | 4 |  | 0-200 | 18 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | Process Gas GAS-111-0036A-CN05-6"-PT |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
44 | TT-2132C | 6" SCH20 | 200 | 240 | 17.1 | 59.9 | 180 |  | 8 |  | 0-200 | 17.1 / 24.5 | 1 1/2", 300# |  | Yes | Direct Mounted |  | GAS-111-0044A-CN05-6"-ET |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
45 | TT-2123C | 6" SCH20 | 200 | 240 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 1 1/2", 600# |  | Yes | Direct Mounted |  | GAS-111-0051A-FN05-6"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Loose Item U Size & rating to be chected by Hirgan Thermowell S.S316 Nace
46 | C-TT-2194C | _ | 500 | 540 | 42.23 | 148 / 149 | 180 |  | 3.5 |  | 0-200 | 54.9 / 62 | 2", 600# |  | Yes | REMOTE TYPE |  | 2nd STAGE DISCHARGE SNUBBER |  |  | BK-GCS-HY-120-PR-PI-0001-Page1 | Rosemount 644HAI1J1M4Q4 | Thermowell S.S316 Nace
47 | C-TT-2204C | 2" TO 4"SCH10 (Expanded) | 150 | 200 | 870 | 60 | 85 |  | 0.3 |  | 0-120 | 5 / 10 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Lube Oil OIL-112-0008A-S.S-2"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
48 | C-TT-2203C | _ | 200 | 250 | 862 | 70 | 85 |  | 1.1 |  | 0-120 | ATM / 10 | 1/2" NPT |  | Yes | REMOTE TYPE |  | crankcase Comp C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3 | Rosemount 644HAI1J1M4Q4
49 | C-TT-2213C | _ | 400 | 450 | 1059 | 70 | 85 |  | - |  | 0-120 | ATM / 7 | 2", 300# |  | Yes | REMOTE TYPE |  | Water Reservoir |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
50 | C-TT-2221C |  |  |  | 1065 | 63 | 85 |  |  |  |  | 3 / 8 | [5 empty] | Cooling water header CWS-112-0002B-C.S-3"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
51 | C-TT-2214C | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor NDE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
52 | C-TT-2215C | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | 0-200 | N/A | N/A |  | Yes | REMOTE TYPE |  | Main Motor DE |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4 | RTD in main motor
53 | C-TT-2216C | Bare block | 2000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp DE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
54 | C-TT-2218C | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp NDE Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
55 | C-TT-2217C | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
56 | C-TT-2219C | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Packing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
57 | C-TT-2220C | Bare block | 1000mm |  |  | N/A | N/A |  | N/A |  | 0-200 | N/A | 3/4" NPT |  | Yes | REMOTE TYPE |  | Comp Mid Bearing |  |  | BK-GCS-HY-120-PR-PI-0001-Page7 | Rosemount 644HAI1J1M4Q4
58 | C-TT-2221C | 3" TO 4"SCH40 (Expanded) | 200 | 250 | 250 | 65 | 85 |  | - |  | 0-120 | ATM / 7 | 1 1/2", 300# |  | Yes | REMOTE TYPE |  | Cooling water header CWS-112-0002C-C.S-3"-IS |  |  | BK-GCS-HY-120-PR-PI-0001-Page5 | Rosemount 644HAI1J1M4Q4
59 | TE-2222C TE-2223C TE-2224C | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor T sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
60 | TE-2225C TE-2226C TE-2227C | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor S sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7
61 | TE-2228C TE-2229C TE-2230C | _ | N/A | N/A | N/A | N/A | N/A |  | N/A |  | RTD Range | N/A | N/A |  | Yes | N/A |  | Main Motor R sensor |  |  | BK-GCS-HY-120-PR-PI-0001-Page7

## DPT
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 10 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V03
Data Sheet for Differential Pressure Transmitter
| 1 | Tag No.: (Refer to Next Page) | Service: (Refer to Next Page)
GENERAL | 2 | Function | Recordo Indicaten Controlo Blindo Transn Intego (Note1)
| 3 | Case | MFR STDn Nom Sizeo Color MFR STDn Other
| 4 | Mounting | Flusho Surfaceo Yoken Other
| 5 | Enclosure Class | General Purposeo Weather Proof n Explosion-Proof o Class
|  |  | For use in Intrinsically Safe Systemn |  |  |  | Other EExia, IIB, T4
| 6 |  | Ingress Protection : IP 66
| 7 | Power Supply | 117 V 60 Hzo Other: aco dcn Volts : 24 VDC Loop Powered
TRANSMITTER | 8 | Trans. Output | 4-20mAn 10-50mAo 21-10 kpa(3-15 psig)o Other 4-20mA Smart HART
| 9 |  | Transmitter Accuracy : Better than 0.1% of Calibrated Span
UNIT | 10 | Service | Flow o Level o Diff. Pressure n Other
| 11 | Element Type | Diaphragmn Helixo Bourdon o Bellowso Other
| 12 | Material | Body Epoxy Painted Die Cast Aluminum Copper free Element 316 S.S. as minimum
| 13 | Range | Fixedo Adj. Range n Set At (Refer to Next Page)
| 14 | Rating | Overrange Protection: at least 1.5 times the maximum range
| 15 | Process Data | Press: Normal Max Element Range (Refer to Next Page)
| 16 | Process Conn. | ½ in. NPTn Other Male with wrench flats
| 17 |  | Location: Bottom n Back o Other
| 18 | Electrical Conn. | MFR STDo Other ISO M20x1.5
OPTIONS | 19 | Miscellaneous | Filt Reg.o Sup. Gageo Output Gageo Charts
| 20 | Diaphragm Seal | Diaph Seal o (N/A) Type : Capillary Length: Mtl. :
Conn. Fill Fluid :
Flushing Connection :
| 21 | Manifold | Valve Manifold : See List
| 22 | MFR. & Model No. | See list
Notes:
1- All transmitters shall be provided complete with LCD type integral indicator .
2- Repeatability of the transmitter shall be better than 0.1% of the span.
3- All transmitters shall be reverse polarity protected.
4- All components, particularly if containing electric contacts, shall be vibration resistant.
5- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## DPT List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 11 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | Bk | GCS | HY | 120 | IN | DS | 0001 | V03
List of DPT
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | DIFFERENTIAL PRESSURE Norm/Max | CALIBRATED RANGE (Barg) | ACCESSORIES | MFR. & Model No. | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Norm. / Design | VISCOSITY (Cst) |  | ACCESSORIES | ACCESSORIES | REV. Remark
1 | PDT-2122A | Process gas Comp A | GAS-111-0031A-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1A | 1/2" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
1 | PDT-2132A | Process gas Comp A | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1A | 1/2" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
2 | C-PDT-2204A | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3A | 1/2" NPT | Liquid | 5 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316 | Rosemount 3051CD3A2B21BB4I1
3 | PDT-2122B | Process gas Comp A | GAS-111-0031A-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1B | 1/2" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
1 | PDT-2132B | Process gas Comp B | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1B | 1/2" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
4 | C-PDT-2204B | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3B | 1/2" NPT | Liquid | 5 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316 | Rosemount 3051CD3A2B21BB4I1
5 | PDT-2122C | Process gas Comp A | GAS-111-0031A-CN05-8"-ET | BK-GCS-HY-120-PR-PI-0001-Page1C | 1/2" NPT | Gas | 4.9 / 22 | 36.8 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
1 | PDT-2132C | Process gas Comp C | GAS-111-0044A-CN05-6"-ET | BK-GCS-HY-120-PR-PI-0001-Page1C | 1/2" NPT | Gas | 17.1 / 22 | 59.9 / 180 | 0.1 / 0.2 | 0-0.4 | Wetted Part S.S316 Nace 5 valve manifold S.S316 | Rosemount 3051CD2A2B21BB4I1 | Loose Item
6 | C-PDT-2204C | Lub Oil Filter | OIL-112-0004A-S.S-2"-NP | BK-GCS-HY-120-PR-PI-0001-Page3C | 1/2" NPT | Liquid | 5 / 10 | 60 / 85 | 0.1 / 0.5 | 0-1 | 5 valve manifold S.S316 | Rosemount 3051CD3A2B21BB4I1
7
8
9
10
11

## DPG
NISOC | [9 empty] | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 | [9 empty] | INSTRUMENT DATASHEETS / CERTIFICATES | [22 empty] | شماره صفحه: 12 از 39
[10 empty] | پروژه |  |  |  |  | بسته کاری |  |  | صادرکننده |  | تسهیلات |  |  | رشته |  |  | نوع مدرک |  |  | سریال |  |  | نسخه
[10 empty] | BK |  |  |  |  | GCS |  |  | HY |  | 120 |  |  | IN |  |  | DS |  |  | 0001 |  |  | V03
Data Sheet for Differential Pressure Gauge
1 | Type : | Direct Rdg. | [5 empty] | 3-15 lb Reciever | [11 empty] | 11 | MFR.& Model No. |  |  |  | Wika 733.51
|  | Other | liquid filled | [16 empty] | 12 | Press Element : Diaphragm | [9 empty] | Bellows
2 | Mounting : | Direct |  |  | Local | [6 empty] | Yoke |  |  |  | Other | [10 empty] | Other | (Note6)
3 | Dial : | Diameter |  | 160 mm |  |  | Color : White / Black Lettering ,Aluminum Non Rusting Metal | [12 empty] | 13 | Element Mtl. : | [5 empty] | Bronze |  |  | Steel
4 | Case : | SS316 |  |  |  |  | Cast Aluminum | [5 empty] | Phenol | [10 empty] | SS |  |  | Other | 316SS
|  | Other | [17 empty] | 14 | Socket Mtl. : | [5 empty] | Bronze |  |  | Steel
5 | Ring : | Screwed |  |  | Hinged |  |  |  |  | Slip | [13 empty] | SS |  |  | Other | 316SS
|  | Std |  |  | Other | [14 empty] | 15 | Connection-NPT : | [5 empty] | 1/4 in. |  |  | 1/2 in. |  |  |  | Other | NPTM
6 | Blow-out Protection : |  |  |  | None |  |  |  | Back |  |  |  | Disc | [13 empty] | Bottom |  |  | Back
|  | Solid Front | [5 empty] | Other | [11 empty] | 16 | Movement: | [5 empty] | Bronze |  |  | SS
7 | Lens : | Glass |  |  | Plastic |  |  | Safety Glass ( shatter proof) | [16 empty] | Naylon |  |  |  | Other |  |  |  | Stainless Steel
8 | Options : | [18 empty] | 17 | Diaphragm Seal |  |  |  | N/A
[5 empty] | Pulsation Dampener | [5 empty] | Refer to note | [11 empty] | MFR. | [8 empty] | Type
[23 empty] | Wetted Part Mtl. | [8 empty] | Other Mtl.
Fill Fluid :
9 | Nominal Accuracy Required : |  |  |  |  | ±1.6% of full scale | [16 empty] | Process Conn. :
10 | Over range protection : |  |  | 1.3 times the maximum scale reading | [15 empty] | 18 | Ingress Protection : | [5 empty] | IP 65
Item | Tag No. |  | Range (barg) |  |  |  | Process Fluid/State | Design | [5 empty] | Operating |  |  |  |  | Differential Pressure |  |  | LINE NO./EQUIPMENTNO. | [6 empty] | P&ID NO. | [6 empty] | Accessories | MFR.& Model | NOTE
[8 empty] | Press (barg) |  |  | Temp (C°) |  |  | Press (barg) |  |  | Temp (C°) |  | Norm. (bar) | Max. (bar)
1 | C-PDG-2204A |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3A | [6 empty] | 5 valve manifold S.S316
2 | C-PDG-2200A |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004A-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4A | [6 empty] | 5 valve manifold S.S316
3 | C-PDG-2201A |  | 0~1 |  |  |  | Instrument Air | 12.5 |  |  | 85 |  |  | 6 |  |  | 65 |  | 0.15 | 0.5 |  | ISA-112-0002A-AZ00-2"-IS | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page2A | [6 empty] | 5 valve manifold S.S316
4 | C-PDG-2205A |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 63 |  | 0.1 | 0.2 |  | CWS-112-0018A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6A | [6 empty] | 5 valve manifold S.S316
5 | C-PDG-2206A |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 63 |  | 0.1 | 0.2 |  | CWS-112-0017A-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6A | [6 empty] | 5 valve manifold S.S316
6 | C-PDG-2204B |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004B-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3B | [6 empty] | 5 valve manifold S.S316
7 | C-PDG-2200B |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004B-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4B | [6 empty] | 5 valve manifold S.S316
8 | C-PDG-2201B |  | 0~1 |  |  |  | Instrument Air | 12.5 |  |  | 85 |  |  | 6 |  |  | 65 |  | 0.15 | 0.5 |  | ISA-112-0002B-AZ00-2"-IS | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page2B | [6 empty] | 5 valve manifold S.S316
9 | C-PDG-2205B |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0018B-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6B | [6 empty] | 5 valve manifold S.S316
10 | C-PDG-2206B |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0017B-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6B | [6 empty] | 5 valve manifold S.S316
11 | C-PDG-2204C |  | 0~1 |  |  |  | Lub Oil Filter | 10 |  |  | 85 |  |  | 6 |  |  | 60 |  | 0.1 | 0.5 |  | OIL-112-0004C-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page3C | [6 empty] | 5 valve manifold S.S316
12 | C-PDG-2200C |  | 0~1 |  |  |  | N2 Gas Supply | 10 |  |  | 85 |  |  | 7.5 |  |  | 60 |  | 0.15 | 0.5 |  | OIL-112-0004C-S.S-2"-NP | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page4C | [6 empty] | 5 valve manifold S.S316
13 | C-PDG-2201C |  | 0~1 |  |  |  | Instrument Air | 12.5 |  |  | 85 |  |  | 6 |  |  | 65 |  | 0.15 | 0.5 |  | ISA-112-0002C-AZ00-2"-IS | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page2C | [6 empty] | 5 valve manifold S.S316
14 | C-PDG-2205C |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0018C-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6C | [6 empty] | 5 valve manifold S.S316
15 | C-PDG-2206C |  | 0~0.6 |  |  |  | Jacket Cooling | 10 |  |  | 85 |  |  | 3 |  |  | 58 |  | 0.1 | 0.2 |  | CWS-112-0017C-C.S-1/2"-PT | [6 empty] | BK-GCS-HY-120-PR-PI-0001-Page6C | [6 empty] | 5 valve manifold S.S316
NOTES :

## PSV (hidden)
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 12 Of 66
1 | ITEM |  |  |  | 1 |  |  |  | 2
2 | TAG NO. |  |  |  | 1601CC001A-PSV-5004A |  |  |  | 1601CC001A-PSV-5005A
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 13 Of 66
1 | ITEM |  |  |  | 3 |  |  |  | 4
2 | TAG NO. |  |  |  | 1601CC001B-PSV-5004B |  |  |  | 1601CC001B-PSV-5005B
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-6 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/H | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 14 Of 66
1 | ITEM |  |  |  | 5 |  |  |  | 6
2 | TAG NO. |  |  |  | 1602CC001A-PSV-5004A |  |  |  | 1602CC001A-PSV-5005A
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 15 Of 66
1 | ITEM |  |  |  | 7 |  |  |  | 8
2 | TAG NO. |  |  |  | 1602CC001B-PSV-5004B |  |  |  | 1602CC001B-PSV-5005B
3 | SERVICE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-12 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | SAFETY & RELIEF |  |  |  | SAFETY & RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | N2 Gas Supply |  |  |  | N2 Gas Supply
29 | REQUIRED CAPACITY |  |  | Nm3/h | 3 |  |  |  | 3
30 | MOL. WT. |  | OPER. SP. GR |  | 28.01 |  | 0.9617 |  | 28.01 | 0.9617
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 1.2 |  | 2 |  | 1.5 | 3
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | AMB |  | AMB |  | AMB | AMB
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  |  |  | ATM
34 |  |  | VARIABLE |  | ATM |  |  |  | ATM
35 |  |  | TOTAL |  | ATM |  |  |  | ATM
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z) |  |  |  | 0.99554 |  |  |  | 0.99554
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg) |  |  |  | - |  |  |  | -
40 | RATIO OF SPECIFIC HEATS (Cp / Cv) |  |  |  | 1.4 |  |  |  | 1.4
41 | OPERATING VISCOSITY cP |  |  |  | 0.020402 |  |  |  | 0.020402
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 16 Of 66
1 | ITEM |  |  |  | 9 |  |  |  | 10
2 | TAG NO. |  |  |  | 1601CC001A-RV-5002A |  |  |  | 1601CC001A-PRV-5003A
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 1"-LBO-160CC001-10004-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | No |  |  |  | No
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | ATM |  | ATM | ATM
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 17 Of 66
1 | ITEM |  |  |  | 11 |  |  |  | 12
2 | TAG NO. |  |  |  | 1601CC001B-RV-5002B |  |  |  | 1601CC001B-PRV-5003B
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 18 Of 66
1 | ITEM |  |  |  | 13 |  |  |  | 14
2 | TAG NO. |  |  |  | 1602CC001A-RV-5002A |  |  |  | 1602CC001A-PRV-5003A
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.
Document No.: |  | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  |  | Contract No.: AP-1-92-92 |  |  |  | Page 19 Of 66
1 | ITEM |  |  |  | 15 |  |  |  | 16
2 | TAG NO. |  |  |  | 1602CC001B-RV-5002B |  |  |  | 1602CC001B-PRV-5003B
3 | SERVICE |  |  |  | Lube Oil |  |  |  | Lube Oil
4 | P&ID NO. |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15 |  |  |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
5 | LINE NO. / VESSEL NO. |  |  |  | 1"-LBO-160CC001-10004-AN41-PT |  |  |  | 3/4"-LBO-160CC001-10003-AN41-PT
6 | FULL NOZZLE, SEMI NOZZLE |  |  |  | FULL NOZZLE |  |  |  | FULL NOZZLE
7 | SAFETY OR RELIEF |  |  |  | RELIEF |  |  |  | RELIEF
8 | CONV., BELLOWS, PILOT OP. |  |  |  | CONVENTIONAL |  |  |  | CONVENTIONAL
9 | BONNET TYPE |  |  |  | CLOSED |  |  |  | CLOSED
CONNECTION
10 | SIZE: INLET |  | OUTLET |  | VTA |  |  | VTA | VTA |  | VTA
11 | FLANGE RATING OR SCRWED: IN |  | OUT |  | 150# ,ASME B 16.5 |  |  | 150# ,ASME B 16.5 | 150# ,ASME B 16.5 |  | 150# ,ASME B 16.5
12 | FACING/ FINISHING : IN |  | OUT |  | (RF) 125 AARH |  |  | (RF) 125 AARH | (RF) 125 AARH |  | (RF) 125 AARH
MATERIALS
13 | BODY & BONNET |  |  |  | A105 OR A216 GR.WCB |  |  |  | A105 OR A216 GR.WCB
14 | SEAT AND DISC |  |  |  | S.S 316 STELLITED |  |  |  | S.S 316 STELLITED
15 | NOZZLE |  |  |  | 316 S.S. |  |  |  | 316 S.S.
16 | RESILIENT SEAT SEAL |  |  |  | PTFE |  |  |  | PTFE
17 | GUID AND RINGS |  |  |  | 316 S.S |  |  |  | 316 S.S
18 | SPRINGS |  |  |  | CARBON STEEL |  |  |  | CARBON STEEL
19 | BELLOWS |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
20 | NACE MATERIAL |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
OPTIONS
21 | CAP : SCREWED OR BOLTED |  |  |  | Screwed |  |  |  | Screwed
22 | LEVER : PLAIN OR PACKED |  |  |  | NOT REQUIRED |  |  |  | NOT REQUIRED
23 | TEST GAG |  |  |  | NO |  |  |  | NO
24 | RUPTURE DISC |  |  |  | NO |  |  |  | NO
BASIS
25 | CODE |  |  |  | API RP 520 |  |  |  | API RP 520
26 | FIRE |  |  |  | NO |  |  |  | NO
27 | OTHER |  |  |  | BLOCK OUTLET |  |  |  | BLOCK OUTLET
FLUID DATA
28 | FLUID & STATE |  |  |  | Lube Oil |  |  |  | Lube Oil
29 | REQUIRED CAPACITY |  |  | Kg/Hr | 2131 |  |  |  | 2131
30 | MOL. WT. |  | OPER. SP. GR |  | 122 |  | 0.8 |  | 122 | 0.8
31 | OPER. PRESS. Barg |  | SET PRESSURE Barg |  | 6 |  | 7 |  | 6 | 7
32 | OPER. TEMP. ˚C |  | REL. TEMP. ˚C |  | 60-80 |  | 80 |  | 60-80 | 80
33 | BACK PRESSURE Barg |  | CONSTANT |  | ATM |  | 6 |  | ATM | 6
34 |  |  | VARIABLE
35 |  |  | TOTAL
36 | % ALLOWABLE OVER PRESS. |  |  |  | 10 |  |  |  | 10
37 | OVER PRESSURE FACTOR |  |  |  | 10% |  |  |  | 10%
38 | COMPRESSIBILITY FACTOR (Z)
39 | LATENT HEAT OF VAPORIZATION (Kj / Kg)
40 | RATIO OF SPECIFIC HEATS (Cp / Cv)
41 | OPERATING VISCOSITY cP |  |  |  | 95-100(ASTM D4292 / ISO 2909) |  |  |  | 95-100(ASTM D4292 / ISO 2909)
42 | barometric pressure |  |  | m bara | 1000 |  |  |  | 1000
43 | CORROSION
44
SPECIFICATION
45 | CALCULATION ORIFICE AREA |  |  | in ²
46 | SELECTED ORIFICE AREA |  |  | in ²
47 | ORIFICE DESIGNATION
48 | MANUFACTURE |  |  |  | Note 1 |  |  |  | Note 1
49 | MODEL NO. |  |  |  | Note 1 |  |  |  | Note 1
50 | MAXIMUM SOUND LEVEL (db) |  |  |  | 115 db @ 1 m |  |  |  | 115 db @ 1 m
Note : 1. : This Item Will be Filled by Vendor.

## TCV (hidden)
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 32 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001A-TCV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 33 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001B-TCV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 34 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001A-TCV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 35 Of 66
General | 1 | Instrument Name |  |  |  | TEMPRETURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001B-TCV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | Lubricant Service |  | 1"-LBO-160CC001-10005-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 60~74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Tempreture Set Point |  |  | VTA |  | 60oC
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point= 60oC
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## PRV (hidden)
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 36 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001A-PRV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 37 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1601CC001B-PRV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 38 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001A-PRV-5001A |  | ARCP-F160HY-ENPU-DIPI-0022-11 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
Document No.: | ARCP-F160HY-ENIN-DSIN-0025-V02 |  |  | Contract No.: AP-1-92-92 |  |  | Page 38 Of 66
General | 1 | Instrument Name |  |  |  | BACK PRESSURE REGULATOR
| 2 | Tag Number | P&ID No. |  |  | 1602CC001B-PRV-5001B |  | ARCP-F160HY-ENPU-DIPI-0022-5 OF 15
| 3 | Service | Pipe No. |  |  | From Auxilary Oil Pump |  | 3/4"-LBO-160CC001-10006-AN41-PT
| 4 | Pipe O. D. /I. D. mm | Pipe Class |  |  | 1" |  | AN41
| 5 | Pipe Material | Pipe Insulation
Process Conditions | 6 | Fluid | State |  |  | LUBRICANT OIL |  | Liquid
| 7 | Design Pressure bar(g) | Max. Shut-Off DP. bar(g) |  |  | 10 |  | 10
| 8 | Operating Temperature ℃ | Design Temperature ℃ |  |  | 74 |  | 120
| 9 | Operating Density kg/m3 | Standard Density kg/Nm3 |  |  | 870
| 10 | Kinetic Viscosity (mm2/S) | Dynamic Viscosity (cP) |  |  | 90 |  | 78.3
| 11 | Speci. Heat Ratio Cp/Cv | Compress Factor |  |  | 1.2
| 12 | Vapor Pressure | Critical Pressure
| 13 |  |  |  | Unit | Min. Flow | Nor. Flow |  | Max. Flow
|  | Flow Rate |  |  | m3/h | 1.55 | 1.55 |  | 1.55
| 14 | Inlet Pressure |  |  | bar(g) | 4 | 6 |  | 7
| 15 | Outlet Pressure |  |  | bar(g) | 4 | 6 |  | 6
Calculation Data | 16 | Sizing Cv |  |  |  |  | VTA
| 17 | Valve Travel |  |  | ％ |  | VTA
| 18 | Allowable SPL dBA | Predicated SPL dBA |  |  | <85 dB |  | VTA
| 19 | Rated Cv | Valve Fl |  |  | VTA |  | VTA
20
Valve Body/Bonnet | 21 | Model |  |  |  | VTA
| 22 | Body Type | Control Mode |  |  | Globe |  | SELF
| 23 | Body Size | End Connection & Rating |  |  | 1/2"(VTC) |  | 1/2",Flange,150# RF
| 24 | Allowable Operating Temperature ℃ | Pressure Rating |  |  | VTA |  | VTA
| 25 | Bonnet Type | Flow Direction |  |  | Bolted |  | VTA
| 26 | Body Material | Stem/Shaft Material |  |  | C.S(A105) |  | Min 316 S.S
27
Trim | 28 | Trim Type | Trim Size |  |  | VTA |  | VTA
| 29 | Trim Material | Seat Material |  |  | 316 S.S |  | 316 S.S
| 30 | Guiding | Packing Material |  |  | VTA |  | PTFE
| 31 | Characteristics | Seat Leakage Class |  |  | EQ% |  | IV
Actuator | 32 | Model | Type |  |  | VTA |  | Spring&Diaphragm
| 33 | Pilot | Restrictor Type |  |  | VTA |  | Internal(VTC)
| 34 | Restrictor Input | Ext. Connection Size |  |  | DOWNSTREAM |  | -
| 35 | Up Inlet Valve | Down Inlet Valve |  |  | - |  | -
| 36 | Seal Type | Spring Material |  |  | VTA |  | VTA
| 37 | Diaph. Temperature Rating | Diaph. Pressure Rating |  |  | VTA |  | VTA
| 38 | Diaphragm Material | Available D. P. |  |  | VTA |  | VTA
| 39 | Spring Range | Pressure Set Point |  |  | VTA |  | 6 Barg
| 40 | Temperature Assembly | Capillary Length |  |  | - |  | -
| 41 | Fail Position | Tubing&Fitting |  |  | Open |  | Min 316 S.S
| 42 | Enclosure Protection |  |  |  | IP65
43
Accessories | 44 | Filter | Mesh Size |  |  | - |  | -
| 45 | Condenser | Check Valve |  |  | - |  | -
| 46 | Inlet Gauge | Control Gauge |  |  | - |  | -
47
Miscell. | 48 | Manufacturer
| 49 | Requisition No.
50
NOTES：
1- set point=6 Barg
2- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## FG(A)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 13 از 39
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200A | [5 empty] | C-FI-2201A |  | C-FI-2202A |  |  |  | C-FI-2203A
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4A | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4A |  | BK-GCS-HY-120-PR-PI-0001-Page4A |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4A
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2 |  |  | 12.5 |  |  | 0.5 | 12.5 | 0.5 |  | 12.5 |  | 2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## FG (B)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 14 از 39
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200B | [5 empty] | C-FI-2201B |  | C-FI-2202B |  |  |  | C-FI-2203B
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4B | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4B |  | BK-GCS-HY-120-PR-PI-0001-Page4B |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4B
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2 |  |  | 12.5 |  |  | 0.5 | 12.5 | 0.5 |  | 12.5 |  | 2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## FG (C)
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 15 از 39
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  |  |  | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN |  |  |  | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW INDICATOR ( ROTAMETER)
GENERAL DATA
1 | TAG NO. |  | C-FI-2200C | [5 empty] | C-FI-2201C |  | C-FI-2202C |  |  |  | C-FI-2203C
2 | QUANTITY |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
3 | P&ID NO. |  | BK-GCS-HY-120-PR-PI-0001-Page4C | [5 empty] | BK-GCS-HY-120-PR-PI-0001-Page4C |  | BK-GCS-HY-120-PR-PI-0001-Page4C |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page4C
4 | SERVICE |  | N2 Gas Supply | [5 empty] | N2 Gas Supply |  | N2 Gas Supply |  |  |  | N2 Gas Supply
5 | LINE NUMBER |  | 1/2" SS316L Tubing | [5 empty] | 1/2" SS316L Tubing |  | 1/2" SS316L Tubing |  |  |  | 1/2" SS316L Tubing
6 | FUNCTION |  | Local Indicator | [5 empty] | Local Indicator |  | Local Indicator |  |  |  | Local Indicator
7 | MOUNTING |  | Inline | [5 empty] | Inline |  | Inline |  |  |  | Inline
FLUID DATA
8 | FLUID |  | N2 Gas | [5 empty] | N2 Gas |  | N2 Gas |  |  |  | N2 Gas
9 | FLUID STATE |  | Gas | [5 empty] | Gas |  | Gas |  |  |  | Gas
10 | MAXIMUM FLOW Nm3/h |  | 3 | [5 empty] | 3 |  | 3 |  |  |  | 3
11 | NORMAL FLOW Nm3/h |  | 1.5 | [5 empty] | 1.5 |  | 1.5 |  |  |  | 1.5
12 | PRESS. OPERATING / DESIGN (BARG) |  | 2 |  |  | 12.5 |  |  | 0.5 | 12.5 | 0.5 |  | 12.5 |  | 2 | 12.5
13 | TEMP. OPERATING / DESIGN ( °C) |  | 60 |  |  | 85 |  |  | 60 | 85 | 60 |  | 85 |  | 60 | 85
14 | DENSITY AT ST. COND. (KG/m3) |  | 1.183 | [5 empty] | 1.183 |  | 1.183 |  |  |  | 1.183
15 | DENSITY AT OP.COND. (KG/m3) |  | 3.251 | [5 empty] | 2.037 |  | 2.037 |  |  |  | 3.251
16 | COMPRESSIBILITY FACTOR (Z) |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1
17 | MOL. WEIGH T | CP/CV | 28 |  |  | 1.4015 |  |  | 28 | 1.4015 | 28 |  | 1.4015 |  | 28 | 1.4015
18 | OPERATING VISCOSITY (CP) |  | ` | [5 empty] | 0.019015 |  | 0.019015 |  |  |  | 0.019015
19 | MAX. PRESSURE DROP @ MAX. FLOW(BAR) |  | min (nil) | [5 empty] | min (nil) |  | min (nil) |  |  |  | min (nil)
ROTAMETER DETAIL
20 | TYPE |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication | [5 empty] | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication |  |  |  | Metal Type Rotameter-Shall be fitted with Magnetic Follower System For Indication
21 | FLANGE SIZE / RATING / FACING |  | 1/2", 150# R.F | [5 empty] | 1/2", 150# R.F |  | 1/2", 150# R.F |  |  |  | 1/2", 150# R.F
22 | RANGE: FROM / TO (Kg/Hr) |  | 3 Nm3/h | [5 empty] | 3 Nm3/h |  | 3 Nm3/h |  |  |  | 3 Nm3/h
23 | SCALE GRADUATION |  | Direct Scale | [5 empty] | Direct Scale |  | Direct Scale |  |  |  | Direct Scale
24 | BODY / FLANGE MATERIAL |  | 316 S.S |  |  | ASTM A182 F316 |  |  | 316 S.S | ASTM A182 F316 | 316 S.S |  | ASTM A182 F316 |  | 316 S.S | ASTM A182 F316
25 | FLOAT EXTENSION MATERIAL |  | 316 S.S | [5 empty] | 316 S.S |  | 316 S.S |  |  |  | 316 S.S
26 | CONNECTION LAYOUT |  | Bottom-Top , Vertical | [5 empty] | Bottom-Top , Vertical |  | Bottom-Top , Vertical |  |  |  | Bottom-Top , Vertical
27 | INGRESS PROTECTION |  | IP 65 | [5 empty] | IP 65 |  | IP 65 |  |  |  | IP 65
28 | ACCURACY |  | ±1.6% of full scale or better. | [5 empty] | ±1.6% of full scale or better. |  | ±1.6% of full scale or better. |  |  |  | ±1.6% of full scale or better.
ACCESSORIES
29 | NEEDLE VALVE |  | No | [5 empty] | No |  | No |  |  |  | No
30 | SWITCH |  | No | [5 empty] | No |  | No |  |  |  | No
PURCHASE
31 | MODEL |  | H250 | [5 empty] | H250 |  | H250 |  |  |  | H250
32 | MANUFACTURE |  | KROHNE | [5 empty] | KROHNE |  | KROHNE |  |  |  | KROHNE

## SG
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 16 از 39
|  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR SIGHT GLASS
DESIGN DATA
1 | Tag Numbers |  |  |  |  | See Next Page
2 | Pipe Material Class |  |  |  |  | C.S
3 | Service |  |  |  |  | Cooling Water
4 | Operating Pressure |  |  |  |  | See List
5 | Operating Temperature |  |  |  |  | See List
6 | Rating |  |  |  |  | See List
7 | Size Range |  |  |  |  | See List
9 | P&ID Reference |  |  |  |  | See List
SPECIFICATIONS
10 | TYPE |  |  |  |  | Rotary
11 | End Connection |  |  |  |  | Flanged R.F
12 | Cover Type |  |  |  |  | Tempered
13 | Installation Requirements |  |  |  |  | Horizontal or Vertical
MATERIALS
15 | Body |  |  |  |  | C.S
16 | Glass Cover |  |  |  |  | TEMPERED GLASS
17 | Gasket |  |  |  |  | KLINGRIT
18 | Bolts / Studs |  |  |  |  | C.S

## SG List
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 17 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
List of Sight Glass
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. | PROCESS CONNECTION | FLUID/ STATE | PRESSURE (Barg) | TEMPERATURE (C) | REMARKS
[5 empty] | PROCESS CONNECTION | FLUID | Oper. / Design | Oper. / Design
1 | C-SG-2200A | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6A | 1/2"#150 | Liquid | 3 / 7 | 70 / 85
2 | C-SG-2201A | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6A | 2.1/2"#150 | Liquid | 3 / 7 | 70 / 85
3 | C-SG-2202A | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6A | 1"#150 | Liquid | 3 / 7 | 70 / 85
4 | C-SG-2203A | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6A | 1/2"#150 | Liquid | 3 / 7 | 70 / 85
5 | C-SG-2200B | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6B | 1/2"#150 | Liquid | 3 / 7 | 70 / 85
6 | C-SG-2201B | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6B | 2.1/2"#150 | Liquid | 3 / 7 | 70 / 85
7 | C-SG-2202B | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6B | 1"#150 | Liquid | 3 / 7 | 70 / 85
8 | C-SG-2203B | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6B | 1/2"#150 | Liquid | 3 / 7 | 70 / 85
9 | C-SG-2200C | Cooling Water | CWR-112-0014A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6C | 1/2"#150 | Liquid | 3 / 7 | 70 / 85
10 | C-SG-2201C | Cooling Water | CWR-112-0015A-C.S-2.1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6C | 2.1/2"#150 | Liquid | 3 / 7 | 70 / 85
11 | C-SG-2202C | Cooling Water | CWR-112-0012A-C.S-1"-PT | BK-GCS-HY-120-PR-PI-0001-Page6C | 1"#150 | Liquid | 3 / 7 | 70 / 85
12 | C-SG-2203C | Cooling Water | CWR-112-0013A-C.S-1/2"-PT | BK-GCS-HY-120-PR-PI-0001-Page6C | 1/2"#150 | Liquid | 3 / 7 | 70 / 85

## FT A1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 18 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1A
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-CN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 / 18.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 1971 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | NA |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2121A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT A2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 19 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2131A |  |  | BK-GCS-HY-120-PR-PI-0001-Page1A
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 1971 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2131A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT A3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 20 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206A |  |  | BK-GCS-HY-120-PR-PI-0001-Page6A
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Kg/h |  |  | 15300 |  | 16830
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 1060 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 1.87
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.1 |  |  | 0.0053
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | - |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | ~ 40 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~100 mbar
Element | 15 | Tag Number |  |  |  |  | C-FE-2206A
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material
Transmitter Unit | 24 | Model |  |  |  |  | Diff pressure
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~16830m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD2A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 21 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1B
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-CN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 / 18.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 5.102 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2121B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 22 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2131B |  |  | BK-GCS-HY-120-PR-PI-0001-Page1B
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2131B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT B3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 23 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206B |  |  | BK-GCS-HY-120-PR-PI-0001-Page6B
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | m3/h |  |  | 15300 |  | 16830
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 1060 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 1.87
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.1 |  |  | 0.0053
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | - |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | ~ 40 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~100 mbar
Element | 15 | Tag Number |  |  |  |  | C-FE-2206B
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~16830m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD2A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C1
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 24 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2121C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1C
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0031A-CN05-8"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 8" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 4.9 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 36.8 / 18.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 5.771 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 0.0115
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.245 |  |  | 0.975
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 5.102 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 97%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2121C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 6mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 8"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C2
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 25 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | FT-2131C |  |  | BK-GCS-HY-120-PR-PI-0001-Page1C
| 2 | Service |  | Pipe No. |  |  | Process gas |  |  | GAS-111-0044A-CN05-6"-ET
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 6" |  |  | SCH.20
| 4 | Pipe Material |  | Pipe Insulation |  |  | ASTM A106 Gr.B |  |  | N/A
Process Conditions | 5 | Fluid |  | State |  |  | Sour Hydrocarbon |  |  | Gas
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 17.1 |  |  | 22
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 59.9 |  |  | 180
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | Nm3/h | 7887 |  | 7918 |  | 8162.9
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 17.35 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | .0126
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.275 |  |  | 0.964
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | 19.76 |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | 24.52 |  |  | 89%
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~10 mbar
Element | 15 | Tag Number |  |  |  |  | FE-2197C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | S.S316-Nace |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 6"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S. (Nace ) |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~8163Nm3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~10 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316-Nace
| 38 | Wetted Part Material |  |  |  |  | S.S316-Nace
| 39 | Drains/Vents Material |  |  |  |  | S.S316-Nace
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD1A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## FT C3
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 26 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
INSTRUMENT DATA SHEET FOR FLOW TRANSMITTER
| 1 | Tag Number |  | P&ID No. |  |  | C-FT-2206C |  |  | BK-GCS-HY-120-PR-PI-0001-Page6C
| 2 | Service |  | Pipe No. |  |  | Water Console |  |  | CWR-112-0010A-C.S-3"-IS
| 3 | Pipe O. D. /I. D. mm |  | Pipe Sch./Thk. |  |  | 3"
| 4 | Pipe Material |  | Pipe Insulation
Process Conditions | 5 | Fluid |  | State |  |  | Water |  |  | Liquid
| 6 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 3 |  |  | 7
| 7 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 58 |  |  | 85
| 8 | Flow Rate |  |  |  | Unit | Min. Flow |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  | m3/h |  |  | 15300 |  | 16830
| 9 | Operating Density kg/m3 |  | Standard Density kg/Nm3 |  |  | 1060 |  |  | -
| 10 | Kinetic Viscosity(mm2/s) |  | Dynamic Viscosity (cP) |  |  | - |  |  | 1.87
| 11 | Specific Heat Ratio Cp/Cv |  | Compress Factor |  |  | 1.1 |  |  | 0.0053
| 12 | Vapor Pressure |  | Vapor Density kg/m3 |  |  | - |  |  | -
| 13 | Molecular Weight |  | Relative Humidity |  |  | ~ 40 |  |  | -
| 14 | Allowable Pressure Drop @ Max. Flow |  |  |  |  | 0~100 mbar
Element | 15 | Tag Number |  |  |  |  | C-FE-2206C
| 16 | Measure Element Type |  |  |  |  | Orifice
| 17 | Measure Element Material |  | Thickness |  |  | 316SS |  |  | 3mm
| 18 | Bore Diameter |  |  |  |  | Hold
| 19 | Connection Type |  | Size |  |  | Flange Weld neck |  |  | 3"
| 20 | Flange Standard |  | Flange Rating |  |  | ASME B16.5 |  |  | ANSI 300#
| 21 | Flange Material |  | Facing |  |  | C.S |  |  | RF
| 22 | Bolt /Nut Material |  | Bolt /Nut Standard |  |  | ASTM A193 Gr.B7M |  |  | ASTM A194 Gr. 2HM
| 23 | Gasket Type & Material |  |  |  |  | Spiral Wound,S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
Transmitter Unit | 24 | Model |  |  |  |  | 3051CD
| 25 | Available Range |  |  |  |  | –623 to 623 mbar
| 26 | Flowmeter Scale |  |  |  |  | 0~16830m3/h
| 27 | Full Scale Differential Pressure (bar) |  |  |  |  | 0~100 mbar
| 28 | Output Signal |  |  |  |  | HART 4-20mA
| 29 | Accuracy |  |  |  |  | 0.2 %
| 30 | Load Resistance |  |  |  |  | minimum loop resistance of 250 ohms
| 31 | Scale Factor |  |  |  |  | Square Root
| 32 | Housing Material |  |  |  |  | Cast aluminum
| 33 | Allowable Static Pressure |  |  |  |  | 250Barg
| 34 | Power Supply |  |  |  |  | 24 V DC Loop Powered
| 35 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 36 | Explosion Proof |  |  |  |  | Exia IIB T3
| 37 | Enclosure Protection |  |  |  |  | IP66
| 38 | Diaphragm Material |  |  |  |  | S.S316
| 38 | Wetted Part Material |  |  |  |  | S.S316
| 39 | Drains/Vents Material |  |  |  |  | S.S316
| 40 | Integral Indicator / Mounting type |  |  |  |  | Yes / Direct
Accessories | 41 | Valve Manifold |  |  |  |  | 5 valve-S.S316
| 42 | Upstream Straight Run |  |  |  |  | 10X
| 43 | Downstream Straight Run |  |  |  |  | 5X
Miscell. | 44 | Manufacturer |  |  |  |  | Rosemount 3051CD2A2B21BB4I1
| 45 | Requisition No.
NOTES：
1) Spiral Wound as per API 601, 316+Graf or CS, Thk 4.5mm with stainless steel winding and flexible graphite filter.
2) Integral orifice with dual D.P Transmitter
VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable

## LG-A
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 27 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213A |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5A
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR A
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 70 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | 1350mm
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | 1250mm
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LG-B
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 28 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213B |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5B
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR B
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 70 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | 1350mm
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | 1250mm
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LG-C
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 29 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Level gauge
| 2 | Tag Number | P&ID No. |  |  |  | C-LG-2213C |  |  |  | BK-GCS-HY-120-PR-PI-0001-Page5C
| 3 | Service | Equipment No. | [7 empty] | TK-2101-WR C
| 4 | Pipe Class | Vessel Material
| 5 | Vessel Class
Process Conditions | 6 | Upper Fluid | Lower Fluid |  |  |  | Air |  |  |  | Water / Gloycol
| 7 | Upper Density kg/m3 | Lower Density kg/m3 |  |  |  | 1.225 |  |  |  | 1063
| 8 | Operating Pressure bar(g) | Design Pressure bar(g) |  |  |  | ATM |  |  |  | 3.5
| 9 | Operating Temperature ℃ | Design Temperature ℃ |  |  |  | 70 |  |  |  | 85
| 10 | Upper/Lower Kinetic Viscosity (mm2/S) |  |  |  |  | -
| 11 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
Body & Cage | 12 | Model/Type |  |  |  |  | Magnetic
| 13 | C to C mm |  |  |  |  | 1350mm
| 14 | Allowable Oper. Temp. ℃ | Pressure Rating
| 15 | Mounting Style | Connection Orientation |  |  |  | External |  |  |  | Side-Side
| 16 | Visible Length mm |  |  |  |  | 1250mm
| 17 | Scale Unit/Material | Accuracy |  |  |  | Cm |  |  |  | 5mm
| 18 | Indicator Type | Indicator Colour |  |  |  | Magnetic |  |  |  | Flag/White & red
| 19 | Chamber Material | Float Material |  |  |  | S.S |  |  |  | S.S
| 20 | Connection Type | Connection Size |  |  |  | Flange |  |  |  | 2"
| 21 | Flange Standard | Flange Rating |  |  |  | ASME |  |  |  | 300
| 22 | Flange Material | Facing |  |  |  | C.S |  |  |  | RF
| 23 | Other Wetted Parts Material |  |  |  |  | S.S
| 24 | Float Dimension | indicator Housing Material |  |  |  | HOLD |  |  |  | S.S
Transmitter/Switch | 25 | Output Signal | Load Resistance |  |  |  | N/A |  |  |  | N/A
| 26 | Switch Type | Switch Quantity |  |  |  | N/A |  |  |  | N/A
| 27 | Contact Form | Contact Rating |  |  |  | N/A |  |  |  | N/A
| 28 | Switch 1 Contact Action |  |  |  |  | N/A
| 29 | Switch 2 Contact Action |  |  |  |  | N/A
| 30 | Calibration Value (for Switch) |  |  |  |  | N/A
| 31 | Power Supply | Electrical Connection |  |  |  | N/A |  |  |  | N/A
| 32 | Explosion Proof | Enclosure Protection |  |  |  | N/A |  |  |  | N/A
| 33 | Housing Material | Integral Indicator |  |  |  | N/A |  |  |  | N/A
34
35
Accessories | 36 | Drain Valve | Drain Valve Material |  |  |  | 1/2"NPT |  |  |  | S.S
| 37 | Vent Valve | Vent Valve Material |  |  |  | N/A |  |  |  | N/A
| 38 | Vent Valve Connection | Vent Valve Size |  |  |  | N/A |  |  |  | N/A
| 39 | Drain Plug | Vent Plug |  |  |  | N/A |  |  |  | N/A
| 40 | Protective Heat Shield |  |  |  |  | N/A
| 41 | Steam Jacket | Jacket Connection Size |  |  |  | N/A |  |  |  | N/A
| 42 | Steam Pressure bar(g) |  |  |  |  | N/A
| 43 | Non Frosting Extension |  |  |  |  | N/A
| 44 | Stilling Well |  |  |  |  | N/A
| 45 | Surge Protection Device |  |  |  |  | N/A
46
Miscell. | 47 | Manufacturer |  |  |  |  | AZARSAM (Eyvaz Technic)
| 48 | Requisition No.
NOTES： VTA : Vendor to advise VTC : Vendor to confirm N/A : Not Applicable
1 . Vendor shall supply and install Swage Nipple 11/2"THREAD(L) × 3/4" PE(S) for vent and drain connections 2. COMPABILITY WITH NACE MR0175/ISO 15156 TO BE CONSIDERED FOR WETTED EQUIPEMNT.

## LTA1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 30 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213A |  |  | BK-GCS-HY-120-PR-PI-0001-Page5A
| 3 | Service |  | Pipe / Equipment No. |  |  | 1601-CC-001A |  |  | TK-2101-WR C
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -6350~6350 mmH20 |  |  | 0-1350mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer |  | Rosemount 3051CD2A2B21BB4I1
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTB1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 31 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213B |  |  | BK-GCS-HY-120-PR-PI-0001-Page5B
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | TK-2101-WR B
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -6350~6350 mmH20 |  |  | 0-1350mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer |  | Rosemount 3051CD2A2B21BB4I1
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTC1
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 32 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2213C |  |  | BK-GCS-HY-120-PR-PI-0001-Page5C
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | TK-2101-WR C
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Water-Glycol / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 1063
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | ATM |  |  | 3.5
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | Upper/Lower Dynamic Viscosity (cP) |  |  |  |  | 0.0209 / 1.87
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -6350~6350 mmH20 |  |  | 0-1350mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20mA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm (VTC) |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer |  | Rosemount 3051CD2A2B21BB4I1
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## Solenoid Valve
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 33 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
Data Sheet for Solenoid Valve
GENERAL | 1 | TAG NO . |  |  | See List
| 2 | SERVICE |  |  | Instrument Air
| 3 | LINE NO, |  |  | See List |  | _
| 4 | QUNTITY |  |  | See List |  | 1
VALVE BODY | 5 | TYPE |  |  | For single acting
| 6 | SIZE- BODY /PORT |  |  | See List
| 7 | RATING & TYPE CONN. |  |  | NPTF
| 8 | MATERIAL -BODY |  |  | Brass
| 9 | MATERIAL -SEAT |  |  | MFR STD
| 10 | MATERIAL -DIAPHRAGM |  |  | N/A
| 11 | OPERATION DIRECT / PILOT |  |  | Pilot operated |  | DIRECT
| 12 | MANUAL RESET |  |  | N/A |  | _
| 13 | MANUAL OPERATOR |  |  | N/A |  | _
| 14 | PAINTING |  |  | N/A
WHEN DEENERGIZED | 15 | 2 WAY VALVE/3 Way |  |  | 3Way
| 16 | NORMALLY OPEN/CLOSE |  |  | TAG C-SV-2201~4A/B/C N.C TAG C-SV-2205A/B/C N.O |  | _
| 17 | EXTERNAL OVERRIDE |  |  | No |  | _
SOLENOID | 18 | ENCLOSURE |  |  | IP 66
| 19 | VOLTAGE/POWER |  |  | 24 VDC /11W
| 20 | STYLE OF COIL |  |  | MFR STD |  | ENCAPSULATED
| 21 | SINGLE OR DOUBLE COIL |  |  | SINGLE |  | SINGLE
| 22 | INSULATION CLASS |  |  | F |  | F
| 23 | ENCLOSURE MATERIAL |  |  | ALUMINUM |  | F
| 24 | CERTIFICATION |  |  | Eex 'd'-IIB-T4 |  | F
| 25 | ELEC. ENTRY |  |  | M20x1.5 ISO |  | M20 ISO
SERVICE CONDITIONS | 26 | FLUID |  |  | Instrument Air
| 27 | OPER.DIFF.MIN (BAR) |  |  | See List
| 28 | OPER.DIFF.MAX (BAR) |  |  | See List |  | 1"
| 29 | TEMP. NORMAL /MAX |  |  | See List |  | 1"
| 30 | SP.GR |  |  | 1.0
| 31 | VISCOSITY |  |  | N/A |  | 4.5/0.928/0.38
| 32 | VALVE CV |  |  | V.T.A |  | 4.5/0.928/0.38
| 33 | MANUFACTURER |  |  | ASCO
| 34 | MODEL NO.
NOTE: VTA:Vendor To Advise N/A:Not Applicable

## List of SOV
NISOC |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 34 از 39
|  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
List of SOV
ITEM NO. | TAG NO. | SERVICE | LINE NO. / EQUIPMENT NO. | P&ID No. |  |  | OPERATING/DESIGNPRESSSURE (Barg) | TEMPERATURE (C) | SOLENOID VALVE SIZE | REMARKS
[7 empty] | Min. / Des. | Norm. / Design
1 | C-SV-2201A | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2A |  |  | 6 / 12.5 | 65 / 85 | 3/8"
2 | C-SV-2202A | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2A |  |  | 6 / 12.5 | 65 / 85 | 3/8"
3 | C-SV-2203A | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2A |  |  | 6 / 12.5 | 65 / 85 | 3/8"
4 | C-SV-2204A | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2A |  |  | 6 / 12.5 | 65 / 85 | 3/8"
5 | C-SV-2205A | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2A |  |  | 6 / 12.5 | 65 / 85 | 1/2"
6 | C-SV-2201B | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2B |  |  | 6 / 12.5 | 65 / 85 | 3/8"
7 | C-SV-2202B | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2B |  |  | 6 / 12.5 | 65 / 85 | 3/8"
8 | C-SV-2203B | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2B |  |  | 6 / 12.5 | 65 / 85 | 3/8"
9 | C-SV-2204B | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2B |  |  | 6 / 12.5 | 65 / 85 | 3/8"
10 | C-SV-2205B | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2B |  |  | 6 / 12.5 | 65 / 85 | 1/2"
11 | C-SV-2201C | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2C |  |  | 6 / 12.5 | 65 / 85 | 3/8"
12 | C-SV-2202C | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2C |  |  | 6 / 12.5 | 65 / 85 | 3/8"
13 | C-SV-2203C | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2C |  |  | 6 / 12.5 | 65 / 85 | 3/8"
14 | C-SV-2204C | Instrument Air | 3/8" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2C |  |  | 6 / 12.5 | 65 / 85 | 3/8"
15 | C-SV-2205C | Instrument Air | 1/2" SS316L Tubing | BK-GCS-HY-120-PR-PI-0001-Page2C |  |  | 6 / 12.5 | 65 / 85 | 1/2"

## LTA2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 35 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200A |  |  | BK-GCS-HY-120-PR-PI-0001-Page3A
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 425mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 1/2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
46
Miscell | 47 | Manufacturer |  | Rosemount 3051CD1A2B21BB4I1
| 48 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTB2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 36 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200B |  |  | BK-GCS-HY-120-PR-PI-0001-Page3B
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 425mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 1/2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
Miscell | 46 | Manufacturer |  | Rosemount 3051CD1A2B21BB4I1
| 47 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## LTC2
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه:37 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
General | 1 | Instrument Name |  |  |  |  | Diff. Press. Level Transmitter
| 2 | Tag Number |  | P&ID No. |  |  | C-LT-2200C |  |  | BK-GCS-HY-120-PR-PI-0001-Page3C
| 3 | Service |  | Pipe / Equipment No. | [5 empty] | crankcase
| 4 | Pipe Class |  | Vessel Material |  |  | -
| 5 | Vessel Class
| 6 | Upper Fluid / Phase |  | Lower Fluid / Phase |  |  | Air / Gas |  |  | Lubricant Oil / Liquid
| 7 | Upper Density(kg/m3) |  | Lower Density(kg/m3) |  |  | 1.225 |  |  | 890
| 8 | Operating Pressure bar(g) |  | Design Pressure bar(g) |  |  | 6 |  |  | 10
| 9 | Operating Temperature ℃ |  | Design Temperature ℃ |  |  | 70 |  |  | 85
| 10 | U/L Dynamic Viscosity (cP) |  |  |  |  | 0.021/0.89
| 11 | C to C mm |  |  |  |  | -
Transmitter | 12 | Model |  |  |  |  | 3051
| 13 | Type |  | Accuracy |  |  | DP level Tranmitter |  |  | +/- 0.1% Full Scale
| 14 | Available Range |  | Calibration Range (bar) |  |  | -635~635mmH2O |  |  | 425mmH2O
| 15 | Output Signal |  | Power Supply |  |  | HART 4-20MA |  |  | 24VDC Loop Powered
| 16 | Load Resistance(Ω) |  |  |  |  | 250 ohms
| 17 | Zero Elevation & Suppression |  |  |  |  | Yes
| 18 | Electrical Connection |  |  |  |  | ISO M20x1.5
| 19 | Explosion Proof |  | Enclosure Protection |  |  | EXia (Zone 2 IIB T4) |  |  | IP65
| 20 | Response Time |  | Housing Material |  |  | N/A |  |  | Epoxy Painted Die Cast Aluminum Copper Free
| 21 | Failure Mode Alarm |  |  |  |  | Up Scale
Sensing & Body | 22 | Element Type |  | Element Material |  |  | Diaphragm |  |  | 316SS
| 23 | Max. Static Pressure (barg) |  | Allowable Oper. Temp. ℃ |  |  | 135barg |  |  | 85 °C
| 24 | Body Material |  | Flange Material |  |  | 316SS |  |  | ASTM A105
| 25 | Process Connection |  | Flange Standard |  |  | 1/2" |  |  | ASME B16.5
| 26 | Overrange Protection |  | Connector Material |  |  | 130 % |  |  | 316SS
| 27 | Vent/Drain Type&Size |  | Vent/Drain Material |  |  | 1/4"NPT |  |  | 316SS
| 28 | Gasket/O-Ring Material |  | Bolts Material |  |  | PTFE |  |  | ASTM A449
Diaphragm Seal | 29 | Seal Type |  |  |  |  | N/A
| 30 | Extended Length |  | Extended Material |  |  | N/A |  |  | N/A
| 31 | Diaphragm Diameter |  | Diaphragm Material |  |  | N/A |  |  | N/A
| 32 | Capillary Material |  | Capillary Length H/L |  |  | N/A |  |  | N/A
| 33 | Capillary Armor Material |  | Fill Fluid |  |  | N/A |  |  | N/A
| 34 | Fill Fluid Temperature Limits |  | Fill Fluid Density |  |  | N/A |  |  | N/A
| 35 | Connection Type |  | Size |  |  | N/A |  |  | N/A
| 36 | Flange Standard |  | Flange Rating |  |  | N/A |  |  | N/A
| 37 | Flange Material |  | Facing |  |  | N/A |  |  | N/A
| 38 | Flushing Connection |  |  |  |  | N/A |  |  | N/A
Indicator | 39 | Indicator Type |  | Display |  |  | Integral LCD type |  |  | Digital
| 40 | Mounting Bracket |  | Remo. Indic. Connection |  |  | No |  |  | YES
Manifold | 41 | Manifold Model |  | Manifold Type |  |  | VTA |  |  | 5 Way
| 42 | Manifold Rating |  | Manifold Material |  |  | Min. CL 3000 |  |  | 316 SS
| 43 | Manifold Connection |  |  |  |  | 1/2" PROCESS SIDE/FLANG INST SIDE
Accessories | 44 | Mounting Bracket |  | Bracket Material |  |  | Yes / 2'' Pipe |  |  | 316SS
| 45 | Add Corrisive Envir. Enclosure |  | Surge Protected Device |  |  | N/A |  |  | N/A
Miscell | 46 | Manufacturer |  | Rosemount 3051CD1A2B21BB4I1
| 47 | Requisition No.
NOTES：
VTA : Vendor To Advise VTC : Vendor To Confirm N/A : Not Applicable

## PS
NISOC |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [11 empty] | شماره صفحه: 38 از 39
|  |  |  | پروژه |  | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
|  |  |  | BK |  | GCS | HY | 120 | IN | DS |  | 0001 |  | V03
Instrument Data Sheet For Pressure Switch
GENERAL | [9 empty] | SWITCH
1 | Press. |  |  |  | Vaccum |  |  |  |  | 8 | Type: |  | Mercury |  |  |  | Snap
| Comp. |  |  |  | Diff. Press. | [7 empty] | Other :
2 |  | Set In Field |  |  |  | Factory Set |  |  |  | 9 | Quantity: |  | Single |  |  |  | Dual
|  | Internal |  |  | External |  |  | Dial |  | 10 | Form: |  | SPST |  |  | SPDT |  |  | DPDT
3 |  | Fixed |  |  | Adj. |  |  | Min. |  |  |  |  | Other:
ELEMENT | [9 empty] | 11 | Max Rating: |  | 10 Amps |  |  | 24vdc
4 | Diaphragm |  |  |  | Bourdon |  |  | Bellows |  |  |  |  | Other:
[10 empty] | 12 | Load: |  | Inductive |  |  |  | Non-Inductive
5 | Material |  |  |  | Aluminum |  |  |  |  | 13 | IP |  | IP66 Exd/IIB T4 |  |  |  |  | SIL Certified
6 | Connection | 1/2"NPT |  |  |  | Other Size : |  |  |  | 14 | Electrical Connection: |  |  |  | M20x1.5
|  | Bottom |  |  |  | Back |  |  |  | 15 | Manufacturer & Model No. |  |  |  |  | Wika
7 |  | Local |  |  | Surface |  |  | Flush |  | 16 | Accessories |  | Manifold 2Valve
Tag No. |  |  | Process Connection |  |  | Adj. Range |  |  | Set Point |  | Pressure |  | Service or Line Number | [5 empty] | Remark
[6 empty] | (Bar G) |  |  | (Bar G) |  | Design | Working
PS-2133A |  |  | 1 " NPT |  |  | 10~100 |  |  | 57 |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204A |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220A |  |  | 1 " NPT |  |  | 0~10 |  |  | 2 |  | 10Bar | 3 Bar | CWS-112-0002A-C.S-3"-IS
PS-2133B |  |  | 1 " NPT |  |  | 10~100 |  |  | 57 |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204B |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220B |  |  | 1 " NPT |  |  | 0~10 |  |  | 2 |  | 10Bar | 3Bar | CWS-112-0002A-C.S-3"-IS
PS-2133C |  |  | 1 " NPT |  |  | 10~100 |  |  | 57 |  | 62Bar | 54.9Bar | GAS-111-0051A-FN05-6"-IS | [5 empty] | Nace material Loose item
C-PS-2204C |  |  | 1 " NPT |  |  | 0~10 |  |  | 1.2 |  | 10Bar | 5 Bar | OIL-112-0008A-S.S-2"-IS
C-PS-2220C |  |  | 1 " NPT |  |  | 0~10 |  |  | 2 |  | 10Bar | 3Bar | CWS-112-0002A-C.S-3"-IS

## TS
NISOC |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | INSTRUMENT DATASHEETS / CERTIFICATES | [7 empty] | شماره صفحه: 39 از 39
|  |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY | 120 | IN | DS | 0001 | V03
Instrument Data Sheet For Temperature Switch
GENERAL
1.TAG.NO |  | C-TS-2191A |  | C-TS-2194A |  | C-TS-2191B |  |  | C-TS-2194B |  | C-TS-2191C | C-TS-2194C
2.Equipment |  | 1ST STAGE DISCHARGE SNUBBER |  | 2ND STAGE DISCHARGE SNUBBER |  | 1ST STAGE DISCHARGE SNUBBER |  |  | 2ND STAGE DISCHARGE SNUBBER |  | 1ST STAGE DISCHARGE SNUBBER | 2ND STAGE DISCHARGE SNUBBER
3.ENCLOSURE MATERIAL |  | Cast Aluminum |  | Cast Aluminum |  | Cast Aluminum |  |  | Cast Aluminum |  | Cast Aluminum | Cast Aluminum
4.SERVICE |  | Gas |  | Gas |  | Gas |  |  | Gas |  | Gas | Gas
5.RANGE |  | 0-200C |  | 0-200'C |  | 0-200'C |  |  | 0-200'C |  | 0-200'C | 0-200'C
6.Ingress Protection |  | IP 66/Exd-IIB-T4 SIL Certified
THERMOWELL
7.TYPE SYSTEM |  | Flnage/RF |  | Flange/RF |  | Flange/RF |  |  | Flange/RF |  | Flange/RF | Flange/RF
8 MATERIAL |  | AISI 316/Nace |  | AISI 316/Nace |  | AISI 316/Nace |  |  | AISI 316/Nace |  | AISI 316/Nace | AISI 316/Nace
9.CONNECTION LOCATION |  | Bottom |  | Bottom |  | Bottom |  |  | Bottom |  | Bottom | Bottom
10.TUBING LENGTH |  | N/A |  | N/A |  | N/A |  |  | N/A |  | N/A | N/A
11.TUBING TYPE & MATERIAL |  | N/A |  | N/A |  | N/A |  |  | N/A |  | N/A | N/A
12.WELL CONN.SIZE & TYPE |  | 2"#300 |  | 2"#600 |  | 2"#300 |  |  | 2"#600 |  | 2"#300 | 2"#600
13.WELL MATERIAL |  | 316 S.S |  | 316 S.S |  | 316 S.S |  |  | 316 S.S |  | 316 S.S | 316 S.S
14.'U' DIMENSION(NOMINAL) |  | 500mm |  | 500mm |  | 500mm |  |  | 500mm |  | 500mm | 500mm
SWITCH
15.TYPE |  | Snap Action |  | Snap Action |  | Snap Action |  |  | Snap Action |  | Snap Action | Snap Action
16.QUANTITY | FORM | 1/DPDT |  | 1/DPDT |  | 1/DPDT |  |  | 1/DPDT |  | 1/DPDT | 1/DPDT
17.ENCLOSURE |  | IP66 |  | IP66 |  | IP66 |  |  | IP66 |  | IP66 | IP66
18.RATING:VOLTS |  | 24 VDC |  | 24 VDC |  | 24 VDC |  |  | 24 VDC |  | 24 VDC | 24 VDC
19.AMPS |  | 2 |  | 2 |  | 2 |  |  | 2 |  | 2 | 5
20.LOAD TYPE |  | INDUCTIVE |  | INDUCTIVE |  | INDUCTIVE |  |  | INDUCTIVE |  | INDUCTIVE | INDUCTIVE
21.DIFF.:FIXED | ADJUST | YES/- |  | YES/- |  | YES/- |  |  | YES/- |  | YES/- | YES/-
22.ELECTRICAL CONNECTION |  | M20*1.5 |  | M20*1.5 |  | M20*1.5 |  |  | M20*1.5 |  | M20*1.5 | M20*1.5
23.Accuracy |  | 1% Of Spna |  | 1% Of Spna |  | 1% Of Spna |  |  | 1% Of Spna |  | 1% Of Spna | 1% Of Spna
SERVICE CONDITIONS
27.TEMP.:OPER 'C |  | 129'C |  | 148'C |  | 129'C |  |  | 148'C |  | 129'C | 148'C
28.PRESS.:OPER BARG |  | 18 |  | 54.9 |  | 18 |  |  | 54.9 |  | 18 | 54.9
29.TRIP POINT 'C |  | 150 |  | 170 |  | 150 |  |  | 170 |  | 150 | 170
30.MANUFACTURER'S MODEL NO. |  | Ashcroft |  | Ashcroft |  | Ashcroft |  |  | Ashcroft |  | Ashcroft | Ashcroft
31.Density (kg/m3) |  | 14.42 |  | 42.23 |  | 14.42 |  |  | 42.23 |  | 14.42 | 42.23