## PAGE1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
CAUSE & EFFECT CHARTS LIST
شماره پیمان: |  | پروژه |  | بسته کاری | صادر کننده | تسهیلات | رشته | رشته | نوع مدرک | سریال | نسخه | نسخه | شماره صفحه: 1 از 14
9184 – 073 - 053 |  | BK |  | GCS | HY | 120 | XX | IN | LI | 0001 | DXX | V03
طرح نگهداشت و افزایش تولید 27 مخزن
CAUSE & EFFECT CHARTS LIST نگهداشت و افزایش تولید میدان نفتی بینک
V03 | JUL.2024 |  | IFR |  | Havayar Co. |  |  |  | M. Fakharian |  |  |  | M. Sadeghian
V02 | MAY.2024 |  | IFR |  | Havayar Co. |  |  |  | M. Fakharian |  |  |  | S. Faramarzpour
V01 | SEP.2023 |  | IFR |  | Havayar Co. |  |  |  | M. Fakharian |  |  |  | S. Faramarzpour
V00 | JUN.2023 |  | IFR |  | Havayar Co. |  |  |  | M. Fakharian |  |  |  | A. M. Mohseni
Rev. | Date |  | Purpose of Issue / Status |  | Prepared by: |  |  |  | Checked by: |  |  |  | Approved by: | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## PAGE2
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
CAUSE & EFFECT CHARTS LIST
شماره پیمان: |  |  |  | پروژه |  |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 2 از 14
9184 – 073 - 053 |  |  |  | BK |  |  | GCS |  | HY |  | 120 |  |  | IN | LI | 0001 | V03
REVISION RECORD SHEET
Page |  | V00 | V01 |  | V02 |  | V03 | V04 |  | V05 |  | V06 | Page | V00 | V01 | V02 | V03 |  | V04 | V05 | V06
1 | X | X | X |  | X |  | X | [5 empty] | 40
2 | X | X | X |  | X |  | X | [5 empty] | 41
3 | X | X | X |  | X |  | X | [5 empty] | 42
4 | X | X | X |  | X |  | X | [5 empty] | 43
5 | X |  | X |  | X |  | X | [5 empty] | 44
6 | X |  |  |  | X |  | X | [5 empty] | 45
7 | X |  |  |  | X |  | X | [5 empty] | 46
8 | X |  |  |  | X |  | X | [5 empty] | 47
9 | X |  |  |  | X |  | X | [5 empty] | 48
10 | X |  |  |  | X |  | X | [5 empty] | 49
11 | X |  |  |  | X |  | X | [5 empty] | 50
12 | X |  |  |  | X |  | X | [5 empty] | 51
13 | X |  |  |  | X |  | X | [5 empty] | 52
14 | X |  |  |  | X |  | X | [5 empty] | 53
15 | X | [11 empty] | 54
16 | X | [11 empty] | 55
17 | X | [11 empty] | 56
18 | X | [11 empty] | 57
19 | X | [11 empty] | 58
20 | X | [11 empty] | 59
21 | X | [11 empty] | 60
22 | X | [11 empty] | 61
23 | X | [11 empty] | 62
24 | X | [11 empty] | 63
25 | X |  |  |  |  | 66 | [6 empty] | 64
26 | X |  |  |  |  | 67 | [6 empty] | 65
27 | X |  |  |  |  | 68 | [6 empty] | 66
28 | X |  |  |  |  | 69 | [6 empty] | 67
29 | X |  |  |  |  | 70 | [6 empty] | 68
30 | X |  |  |  |  | 71 | [6 empty] | 69
31 | X |  |  |  |  | 72 | [6 empty] | 70
32 | X |  |  |  |  | 73 | [6 empty] | 71
33 | X |  |  |  |  | 74 | [6 empty] | 72
34 | X |  |  |  |  | 75 | [6 empty] | 73
35 | X |  |  |  |  | 76 | [6 empty] | 74
36 | X |  |  |  |  | 77 | [6 empty] | 75
37 | X |  |  |  |  | 78 | [6 empty] | 76
38 | X |  |  |  |  | 79 | [6 empty] | 77
39 | X |  |  |  |  | 80 | [6 empty] | 78

## SD A
START AND SHUTDOWN OF COMPRESSOR A EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C-2101 / C-2102
[7 empty] | EFFECT | FEED BACK ESD | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | SPILL BACK SV | MAIN MOTOR START | MAIN MOTOR STOP | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER ON | CRANCK CASE HEATER OFF | AUX. WATER PUMP START | AUX. WATER PUMP STOP | MAIN WATER PUMP START | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER START | WATER RESERVOIR HEATER STOP | Lubricator pump START | Lubricator pump STOP | COMMON SHUT DOWN LAMP LCP | LUBRICATOR HEATER START | LUBRICATOR HEATER STOP | LUBE OIL COOLER FAN 1 START | LUBE OIL COOLER FAN 2 START | LUBE OIL COOLER FAN 1 STOP | LUBE OIL COOLER FAN 2 STOP | COOLING WATER COOLER FAN START | COOLING WATER COOLER FAN STOP
[7 empty] | TAG NO. | USD-05A | PSOV-2201A | PSOV-2202A | PSOV-2203A | PSOV-2204A | PSOV-2205A | PSOV-2123A | XSS-2224A | XSP-2224A | XSS-2202A | XSP-2202A (NOTE 2) | XSS-2203A | XSP-2203A | XSS-2221A | XSP-2221A | XSS-2222A | XSP-2222A | XSS-2223A | XSP-2223A | XSS-2201A | XSP-2201A (NOTE 2) | ESDL-2230A | XSS-2200A | XSP-2200A | XSS-2205A | XSS-2206A | XSP-2205A | XSP-2206A | XSS-2220A | XSP-2220A
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP | UCP | UCP | UCP | UCP | UCP | UCP | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | LCP | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC
SOUR GAS RECIPROCATING COMPRESSOR | C-2101 / C-2102 | ESD-01A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | CLIENT ESD SIGNAL | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-02 | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | CLIENT ESD SIGNAL | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-02A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | CLIENT ESD SIGNAL | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-2231 A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON UCP | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-2230 A | BK-GCS-HY-120-IN-DW-0006 | 8A of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON LCP | I-60A | LCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TS-2191 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TS-2194 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2133 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE DISCHARGE LINE PRESSURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL PRESSURE LOW LOW | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2220 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER LINE PRESSURE LOW LOW | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2221 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2201 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2202 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2216 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | BEARING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2217 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | PACKING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2218 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | BEARING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2220 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MID BEARING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2219 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | PACKING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2214 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2215 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2222 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2225 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2228 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH HIGH | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2243 A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | COMPRESSOR START P.B ON UCP |  | UCP 2101A | [7 empty] | E (Note1) |  | E |  | E |  |  |  | E |  | E |  | E |  |  | E |  | E | E |  |  | E
|  | HSP-2243 A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | COMPRESSOR STOP P.B ON UCP | I-60A | UCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2234 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | COMPRESSOR START P.B ON LCP | I-60A | LCP 2101A | [7 empty] | E (Note3)
|  | HSP-2234 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | COMPRESSOR STOP P.B ON LCP | I-60A | LCP 2101A | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2231 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | AUXILLIARY OIL PUMP MOTOR START P.B ON LCP | I-20A | LCP 2101A | [9 empty] | E
|  | HSP-2231 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | AUXILLIARY OIL PUMP MOTOR STOP P.B ON LCP | I-20A | LCP 2101A | [10 empty] | E
|  | HST-2230 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL HEATER START P.B ON LCP | I-30A | LCP 2101A | [11 empty] | E
|  | HSP-2230 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL HEATER STOP P.B ON LCP | I-30A | LCP 2101A | [12 empty] | E
|  | HST-2237 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | AUXILLIARY WATER PUMP MOTOR START P.B ON LCP | I-25A | LCP 2101A | [13 empty] | E
|  | HSTP2237 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | AUXILLIARY WATER PUMP MOTOR STOP P.B ON LCP | I-25A | LCP 2101A | [14 empty] | E
|  | HST-2236 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | MAIN WATER PUMP MOTOR START P.B ON LCP | I-22A | LCP 2101A | [15 empty] | E
|  | HSP-2236 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | MAIN WATER PUMP MOTOR STOP P.B ON LCP | I-22A | LCP 2101A | [16 empty] | E
|  | HST-2238 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | WATER HEATER START P.B ON LCP | I-26A | LCP 2101A | [17 empty] | E
|  | HSP-2238 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | WATER HEATER STOP P.B ON LCP | I-26A | LCP 2101A | [18 empty] | E
|  | HST-2233 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | LUBRICATOR MOTOR START P.B ON LCP |  | LCP 2101A | [19 empty] | E
|  | HSP-2233 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | LUBRICATOR MOTOR STOP P.B ON LCP |  | LCP 2101A | [20 empty] | E
|  | HST-2232 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | LUBRICATOR HEATER ON P.B ON LCP |  | LCP 2101A | [22 empty] | E
|  | HSP-2232 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | LUBRICATOR HEATER OFF P.B ON LCP |  | LCP 2101A | [23 empty] | E
|  | HST-2235 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL COOLER MOTOR A START P.B ON LCP |  | LCP 2101A | [24 empty] | E
|  | HSP-2235 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL COOLER MOTOR A STOP P.B ON LCP |  | LCP 2101A | [26 empty] | E
|  | HST-2242 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL COOLER MOTOR B START P.B ON LCP |  | LCP 2101A | [25 empty] | E
|  | HSP-2242 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | OIL COOLER MOTOR B STOP P.B ON LCP |  | LCP 2101A | [27 empty] | E
|  | HST-2239 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | WATER COOLER MOTOR A START ON LCP |  | LCP 2101A | [28 empty] | E
|  | HSP-2239 A | BK-GCS-HY-120-IN-DW-0006 | 08A of 10 | WATER COOLER MOTOR A STOP ON LCP |  | LCP 2101A | [29 empty] | E
|  | VS-2205 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBE OIL AIR COOLER FAN 1 VIBRATION HIGH HIGH | I-62A | UCP 2101A | [26 empty] | E
|  | VS-2206 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBE OIL AIR COOLER FAN 2 VIBRATION HIGH HIGH | I-61A | UCP 2101A | [27 empty] | E
|  | VS-2207 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER AIR COOLER FAN VIBRATION HIGH HIGH | I-63A | UCP 2101A | [29 empty] | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: THE START PERMISSIVE REQUEST FROM UCP TO DCS, START PERMISSION OF UCP, AND START SEQUENCE (AUTOMATICALLY) SHALL BE CONSIDERED WHEN THE COMPRESSOR START IS FROM UCP. NOTE 2: DURING THE COMPRESSOR STOP, WILL BE STOPPED WITH DELAY TIME. NOTE 3: BEFORE STARTING THE COMPRESSOR FROM LCP, PREHEATING AND PRELUBRICATION STEPS (DISCUSSED IN CONTROL PHILOSOPHY"BK-GCS-HY-120-PR-PH-0001") SHALL BE DONE BY OPERATOR VIA LCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 3 از 14
CAUSE AND EFFECT CHARTS LIST

## Alarm A
ALARM SIGNALS OF COMPRESSOR A EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C2101 / C-2102
[7 empty] | EFFECT | COMMON ALARM LAMP LCP
[7 empty] | TAG NO. | XF-2230A
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | LCP
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | PDT-2122 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 1ST STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101A | E
|  | PT-2123 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 1ST STAGE SUCTION PRESSURE HIGH |  | UCP 2101A | E
|  | TT-2191 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101A | E
|  | PT-2124 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 1ST STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101A | E
|  | PT-2132 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE SUCTION PRESSURE LOW |  | UCP 2101A | E
|  | TT-2194 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101A | E
|  | PT-2133 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101A | E
|  | PT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBRICATOR PRESSURE LOW |  | UCP 2101A | E
|  | PDT-2132 A | BK-GCS-HY-120-IN-DW-0006 | 1A of 10 | 2ND STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101A | E
|  | LT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | CRANK CASE LUBE OIL LEVEL LOW |  | UCP 2101A | E
|  | PDT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL FILTER DIFFERENTIAL PRESSURE HIGH |  | UCP 2101A | E
|  | PT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL PRESSURE LOW |  | UCP 2101A | E
|  | TT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL TEMPERATURE LOW |  | UCP 2101A | E
|  | PT-2210 A | BK-GCS-HY-120-IN-DW-0006 | 4A of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101A | E
|  | PT-2211 A | BK-GCS-HY-120-IN-DW-0006 | 4A of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101A | E
|  | PT-2212 A | BK-GCS-HY-120-IN-DW-0006 | 4A of 10 | N2 PURGE PRESSURE HIGH |  | UCP 2101A | E
|  | LT-2213 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER RESERVOIR LEVEL LOW |  | UCP 2101A | E
|  | PT-2220 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER PRESSURE LOW |  | UCP 2101A | E
|  | PT-2220 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER PRESSURE HIGH |  | UCP 2101A | E
|  | TT-2221 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER TEMPERATURE LOW |  | UCP 2101A | E
|  | TT-2221 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2214 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2215 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2216 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2217 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2218 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2219 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101A | E
|  | TT-2220 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MID BEARING TEMPERATURE HIGH |  | UCP 2101A | E
|  | ZT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | 1ST STAGE ROD DROP HIGH |  | UCP 2101A | E
|  | ZT-2201 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | 2ND STAGE ROD DROP HIGH |  | UCP 2101A | E
|  | VT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | FRAME VIBRATION HIGH |  | UCP 2101A | E
|  | VT-2201 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | FRAME VIBRATION HIGH |  | UCP 2101A | E
|  | VT-2202 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | FRAME VIBRATION HIGH |  | UCP 2101A | E
|  | TE-2222 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH |  | UCP 2101A | E
|  | TE-2225 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH |  | UCP 2101A | E
|  | TE-2228 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH |  | UCP 2101A | E
|  | XT-2200 A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | KEY PHASOR ROTATION SPEED HIGH |  | UCP 2101A | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 4 از 14
CAUSE AND EFFECT CHARTS LIST

## Start permission A
ALARM SIGNALS OF COMPRESSOR A EFFECTS CAUSE
[7 empty] | EFFECT | Ready to start | COMPRESSOR START PERMISSION LAMP
[7 empty] | TAG NO. | XR-2231A | XSP-2230 A
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP | LCP
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | XF-2230A | BK-GCS-HY-120-IN-DW-0006 | 8A of 10 | NO COMMON ALARM (Lamp Off) |  | LCP 2101 A | DE | DE
|  | ESDL-2230A | BK-GCS-HY-120-IN-DW-0006 | 8A of 10 | NO COMMON SHUTDOWN (Lamp Off) |  | LCP 2101 A | DE | DE
|  | XR-2231A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | AXU. OIL PUMP MOTOR RUN FEED BACK |  | LCP 2101 A | E | E
|  | PT-2204A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBE OIL PRESSURE |  | UCP 2101 A | E
|  | TT-2204A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBE OIL TEMPERATURE |  | UCP 2101 A | E
|  | PT-2220A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER PRESSURE |  | UCP 2101 A | E
|  | TT-2221A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER TEMPERATURE |  | UCP 2101 A | E
|  | CZSO-2225A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | BARING DEVICE UNLOCK FEED BACK (ON) |  | UCP 2101 A | E
|  | XF-2224A | BK-GCS-HY-120-IN-DW-0006 | 7A of 10 | NO MAIN MOTOR FAULT |  | UCP 2101 A | E
|  | PT-2210A | BK-GCS-HY-120-IN-DW-0006 | 4A of 10 | PRESSURE PACKING N2 PRESSURE |  | UCP 2101 A | E
|  | PT-2211A | BK-GCS-HY-120-IN-DW-0006 | 4A of 10 | ROD PACKING N2 PRESSURE |  | UCP 2101 A | E
|  | LT-2200A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUBE OIL LEVEL |  | UCP 2101 A | E
|  | PSOV-2201A PSOV-2202A PSOV-2203A PSOV-2204A PSOV-2205A | BK-GCS-HY-120-IN-DW-0006 | 2A of 10 | CAPACITY SWITCH ON 0% LOAD (DE ENERGIZED) |  | UCP 2101 A | E
|  | HSS-2125A | BK-GCS-HY-120-IN-DW-0006 | 9A of 10 | CLIENT PERMISSIVE TO START (NOTE 1) |  | UCP 2101 A | E | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: A REQUEST PERMISSION SIGNAL (HSS-2126A) FROM UCP WILL BE SENT TO DCS, THEN START PERMISSIOM SIGNAL (HSS-2125A) FROM DCS WILL BE SENT TO UCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 5 از 14
CAUSE AND EFFECT CHARTS LIST

## Control A
CONTROL SIGNALS OF COMPRESSOR A EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C-2101 / C-2102
[7 empty] | EFFECT | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER ON | CRANCK CASE HEATER OFF | AUX. WATER PUMP START | AUX. WATER PUMP STOP | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER START | WATER RESERVOIR HEATER STOP | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR
[7 empty] | TAG NO. | XSS-2202A (Note1) | XSP-2202A | XSS-2203A | XSP-2203A | XSS-2221A | XSP-2221A | XSP-2222A | XSS-2223A | XSP-2223A | PSOV-2201A | PSOV-2202A | PSOV-2203A | PSOV-2204A | PSOV-2205A
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | UCP 2101A | UCP 2101A | UCP 2101A | UCP 2101A | UCP 2101A
|  | TT-2203 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | CRANK CASE LUB OIL TEMPERATURE HIGH | I-30A | UCP 2101A |  |  |  | E
|  | TT-2203 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | CRANK CASE LUB OIL TEMPERATURE LOW | I-30A | UCP 2101A |  |  | E
|  | PT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL PRESSURE HIGH | I-20A | UCP 2101A |  | E
|  | PT-2204 A | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LUB OIL PRESSURE LOW | I-20A | UCP 2101A | E
|  | LT-2213 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER RESERVOIR LEVEL LOW LOW | I-22A | UCP 2101A | [5 empty] | E | E
|  | TT-2213 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER RESERVOIR TEMPERATURE LOW | I-26A | UCP 2101A | [7 empty] | E
|  | TT-2213 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER RESERVOIR TEMPERATURE HIGH | I-26A | UCP 2101A | [8 empty] | E
|  | PT-2220 A | BK-GCS-HY-120-IN-DW-0006 | 5A of 10 | COOLING WATER LINE PRESSURE LOW | I-25A | UCP 2101A |  |  |  |  | E
|  | HSL-2242 A1 | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LOAD 0% SELECTOR SWITCH ON UCP | I-40A | UCP 2101A | [9 empty] | DE | DE | DE | DE | DE
|  | HSL-2242 A2 | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LOAD 25% SELECTOR SWITCH ON UCP | I-40A | UCP 2101A | [9 empty] | E | DE | DE | E | E
|  | HSL-2242 A3 | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LOAD 50% SELECTOR SWITCH ON UCP (NOTE 1) | I-40A | UCP 2101A | [9 empty] | DE | E | DE | E | DE
|  | HSL-2242 A4 | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LOAD 75% SELECTOR SWITCH ON UCP | I-40A | UCP 2101A | [9 empty] | E | E | E | E | E
|  | HSL-2242 A5 | BK-GCS-HY-120-IN-DW-0006 | 3A of 10 | LOAD 100% SELECTOR SWITCH ON UCP | I-40A | UCP 2101A | [9 empty] | E | E | E | E | DE
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: THE CRANK-END (PSOV-2201 A / 2204 A) AND HEAD-END (PSOV-2202 A / 2203 A) SIDES WILL BE CHANGED ALTERNATELY AS MENTIONED IN CONTROL PHILOSOPHY ("BK-GCS-HY-120-PR-PH-0001").
\
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 6 از 14
CAUSE AND EFFECT CHARTS LIST

## Messages (hidden)
Oval 931 | Sht 1
Oval 936 | Sht 1
Oval 1656 | Sht 1
Oval 87 | Sht 2
Oval 93 | Sht 2
Oval 94 | Sht 2
Oval 96 | Sht 2
Oval 502 | Sht 2
Oval 102 | Sht 2
Oval 89 | Sht 2
Oval 161 | Sht 4
Oval 525 | Sht 4
Oval 299 | Sht 4
Oval 209 | Sht 4
Rectangle 229 | Sht 4
Oval 241 | Sht 4
Oval 356 | Sht 5
Oval 349 | Sht 5
Oval 350 | Sht 5
Oval 581 | Sht 5
Oval 70 | Sht 11
Oval 71 | Sht 11
Oval 193 | Sht 12
Oval 192 | Sht 12
Oval 206 | Sht 12
Oval 196 | Sht 12
Oval 276 | Sht 13
Oval 277 | Sht 13
Oval 289 | Sht 13
Oval 321 | Sht 14
Oval 326 | Sht 14
Oval 546 | Sht 14
Oval 355 | Sht 14
Oval 358 | Sht 14
Oval 361 | Sht 14
Oval 369 | Sht 14
Oval 363 | Sht 14
Oval 371 | Sht 14
Oval 364 | Sht 14
Oval 372 | Sht 14