## SD B
START AND SHUTDOWN OF COMPRESSOR B EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C-2101 / C-2102
[7 empty] | EFFECT | FEED BACK ESD | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | SPILL BACK SV | MAIN MOTOR START | MAIN MOTOR STOP | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER ON | CRANCK CASE HEATER OFF | AUX. WATER PUMP START | AUX. WATER PUMP STOP | MAIN WATER PUMP START | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER START | WATER RESERVOIR HEATER STOP | Lubricator pump START | Lubricator pump STOP | COMMON SHUT DOWN LAMP LCP | LUBRICATOR HEATER START | LUBRICATOR HEATER STOP | LUBE OIL COOLER FAN 1 START | LUBE OIL COOLER FAN 2 START | LUBE OIL COOLER FAN 1 STOP | LUBE OIL COOLER FAN 2 STOP | COOLING WATER COOLER FAN START | COOLING WATER COOLER FAN STOP
[7 empty] | TAG NO. | USD-05B | PSOV-2201B | PSOV-2202B | PSOV-2203B | PSOV-2204B | PSOV-2205B | PSOV-2123B | XSS-2224B | XSP-2224B | XSS-2202B | XSP-2202B (NOTE 2) | XSS-2203B | XSP-2203B | XSS-2221B | XSP-2221B | XSS-2222B | XSP-2222B | XSS-2223B | XSP-2223B | XSS-2201B | XSP-2201B (NOTE 2) | ESDL-2230B | XSS-2200B | XSP-2200B | XSS-2205B | XSS-2206B | XSP-2205B | XSP-2206B | XSS-2220B | XSP-2220B
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP | UCP | UCP | UCP | UCP | UCP | UCP | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | LCP | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC
SOUR GAS RECIPROCATING COMPRESSOR | C-2101 / C-2102 | ESD-01A | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | CLIENT ESD SIGNAL | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-02 | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | CLIENT ESD SIGNAL | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-02A | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | CLIENT ESD SIGNAL | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-2231 B | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON UCP | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | ESD-2230 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON LCP | I-60B | LCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TS-2191 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TS-2194 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2133 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE DISCHARGE LINE PRESSURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL PRESSURE LOW LOW | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | PS-2220 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER LINE PRESSURE LOW LOW | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2221 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2201 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | VT-2202 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2216 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | BEARING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2217 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | PACKING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2218 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | BEARING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2220 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MID BEARING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2219 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | PACKING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2214 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2215 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2222 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2225 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | TT-2228 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH HIGH | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2243 B | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | COMPRESSOR START P.B ON UCP |  | UCP 2101B | [7 empty] | E (Note1) |  | E |  | E |  |  |  | E |  | E |  | E |  |  | E |  | E | E |  |  | E
|  | HSP-2243 B | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | COMPRESSOR STOP P.B ON UCP | I-60B | UCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2234 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | COMPRESSOR START P.B ON LCP | I-60B | LCP 2101B | [7 empty] | E (Note3)
|  | HSP-2234 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | COMPRESSOR STOP P.B ON LCP | I-60B | LCP 2101B | E | DE | DE | DE | DE | DE | DE |  | E | E | E |  | E |  | E |  | E |  | E |  | E | E |  | E |  |  | E | E |  | E
|  | HST-2231 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | AUXILLIARY OIL PUMP MOTOR START P.B ON LCP | I-20B | LCP 2101B | [9 empty] | E
|  | HSP-2231 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | AUXILLIARY OIL PUMP MOTOR STOP P.B ON LCP | I-20B | LCP 2101B | [10 empty] | E
|  | HST-2230 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL HEATER START P.B ON LCP | I-30B | LCP 2101B | [11 empty] | E
|  | HSP-2230 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL HEATER STOP P.B ON LCP | I-30B | LCP 2101B | [12 empty] | E
|  | HST-2237 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | AUXILLIARY WATER PUMP MOTOR START P.B ON LCP | I-25B | LCP 2101B | [13 empty] | E
|  | HSTP2237 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | AUXILLIARY WATER PUMP MOTOR STOP P.B ON LCP | I-25B | LCP 2101B | [14 empty] | E
|  | HST-2236 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | MAIN WATER PUMP MOTOR START P.B ON LCP | I-22B | LCP 2101B | [15 empty] | E
|  | HSP-2236 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | MAIN WATER PUMP MOTOR STOP P.B ON LCP | I-22B | LCP 2101B | [16 empty] | E
|  | HST-2238 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | WATER HEATER START P.B ON LCP | I-26B | LCP 2101B | [17 empty] | E
|  | HSP-2238 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | WATER HEATER STOP P.B ON LCP | I-26B | LCP 2101B | [18 empty] | E
|  | HST-2233 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | LUBRICATOR MOTOR START P.B ON LCP |  | LCP 2101B | [19 empty] | E
|  | HSP-2233 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | LUBRICATOR MOTOR STOP P.B ON LCP |  | LCP 2101B | [20 empty] | E
|  | HST-2232 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | LUBRICATOR HEATER ON P.B ON LCP |  | LCP 2101B | [22 empty] | E
|  | HSP-2232 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | LUBRICATOR HEATER OFF P.B ON LCP |  | LCP 2101B | [23 empty] | E
|  | HST-2235 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL COOLER MOTOR A START P.B ON LCP |  | LCP 2101B | [24 empty] | E
|  | HSP-2235 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL COOLER MOTOR A STOP P.B ON LCP |  | LCP 2101B | [26 empty] | E
|  | HST-2242 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL COOLER MOTOR B START P.B ON LCP |  | LCP 2101B | [25 empty] | E
|  | HSP-2242 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | OIL COOLER MOTOR B STOP P.B ON LCP |  | LCP 2101B | [27 empty] | E
|  | HST-2239 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | WATER COOLER MOTOR A START ON LCP |  | LCP 2101B | [28 empty] | E
|  | HSP-2239 B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | WATER COOLER MOTOR A STOP ON LCP |  | LCP 2101B | [29 empty] | E
|  | VS-2205 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBE OIL AIR COOLER FAN 1 VIBRATION HIGH HIGH | I-62B | UCP 2101B | [26 empty] | E
|  | VS-2206 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBE OIL AIR COOLER FAN 2 VIBRATION HIGH HIGH | I-61B | UCP 2101B | [27 empty] | E
|  | VS-2207 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER AIR COOLER FAN VIBRATION HIGH HIGH | I-63B | UCP 2101B | [29 empty] | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: THE START PERMISSIVE REQUEST FROM UCP TO DCS, START PERMISSION OF UCP, AND START SEQUENCE (AUTOMATICALLY) SHALL BE CONSIDERED WHEN THE COMPRESSOR START IS FROM UCP. NOTE 2: DURING THE COMPRESSOR STOP, WILL BE STOPPED WITH DELAY TIME. NOTE 3: BEFORE STARTING THE COMPRESSOR FROM LCP, PREHEATING AND PRELUBRICATION STEPS (DISCUSSED IN CONTROL PHILOSOPHY"BK-GCS-HY-120-PR-PH-0001") SHALL BE DONE BY OPERATOR VIA LCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 7 از 14
CAUSE AND EFFECT CHARTS LIST

## Alarm B
ALARM SIGNALS OF COMPRESSOR B EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C2101 / C-2102
[7 empty] | EFFECT | COMMON ALARM LAMP LCP
[7 empty] | TAG NO. | XF-2230B
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | LCP
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | PDT-2122 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 1ST STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101B | E
|  | PT-2123 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 1ST STAGE SUCTION PRESSURE HIGH |  | UCP 2101B | E
|  | TT-2191 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101B | E
|  | PT-2124 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 1ST STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101B | E
|  | PT-2132 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE SUCTION PRESSURE LOW |  | UCP 2101B | E
|  | TT-2194 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101B | E
|  | PT-2133 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101B | E
|  | PT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBRICATOR PRESSURE LOW |  | UCP 2101B | E
|  | PDT-2132 B | BK-GCS-HY-120-IN-DW-0006 | 1B of 10 | 2ND STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101B | E
|  | LT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | CRANK CASE LUBE OIL LEVEL LOW |  | UCP 2101B | E
|  | PDT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL FILTER DIFFERENTIAL PRESSURE HIGH |  | UCP 2101B | E
|  | PT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL PRESSURE LOW |  | UCP 2101B | E
|  | TT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL TEMPERATURE LOW |  | UCP 2101B | E
|  | PT-2210 B | BK-GCS-HY-120-IN-DW-0006 | 4B of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101B | E
|  | PT-2211 B | BK-GCS-HY-120-IN-DW-0006 | 4B of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101B | E
|  | PT-2212 B | BK-GCS-HY-120-IN-DW-0006 | 4B of 10 | N2 PURGE PRESSURE HIGH |  | UCP 2101B | E
|  | LT-2213 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER RESERVOIR LEVEL LOW |  | UCP 2101B | E
|  | PT-2220 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER PRESSURE LOW |  | UCP 2101B | E
|  | PT-2220 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER PRESSURE HIGH |  | UCP 2101B | E
|  | TT-2221 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER TEMPERATURE LOW |  | UCP 2101B | E
|  | TT-2221 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2214 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2215 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2216 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2217 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2218 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2219 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101B | E
|  | TT-2220 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MID BEARING TEMPERATURE HIGH |  | UCP 2101B | E
|  | ZT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | 1ST STAGE ROD DROP HIGH |  | UCP 2101B | E
|  | ZT-2201 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | 2ND STAGE ROD DROP HIGH |  | UCP 2101B | E
|  | VT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | FRAME VIBRATION HIGH |  | UCP 2101B | E
|  | VT-2201 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | FRAME VIBRATION HIGH |  | UCP 2101B | E
|  | VT-2202 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | FRAME VIBRATION HIGH |  | UCP 2101B | E
|  | TE-2222 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH |  | UCP 2101B | E
|  | TE-2225 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH |  | UCP 2101B | E
|  | TE-2228 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH |  | UCP 2101B | E
|  | XT-2200 B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | KEY PHASOR ROTATION SPEED HIGH |  | UCP 2101B | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 8 از 14
CAUSE AND EFFECT CHARTS LIST

## Start permission B
ALARM SIGNALS OF COMPRESSOR B EFFECTS CAUSE
[7 empty] | EFFECT | Ready to start | COMPRESSOR START PERMISSION LAMP
[7 empty] | TAG NO. | XR-2231B | XSP-2230 B
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP | LCP
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | XF-2230B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | NO COMMON ALARM (Lamp Off) |  | UCP 2101 B | DE | DE
|  | ESDL-2230B | BK-GCS-HY-120-IN-DW-0006 | 8B of 10 | NO COMMON SHUTDOWN (Lamp Off) |  | UCP 2101 B | DE | DE
|  | XR-2231B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | AXU. OIL PUMP MOTOR RUN FEED BACK |  | UCP 2101 B | E | E
|  | PT-2204B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBE OIL PRESSURE |  | UCP 2101 B | E
|  | TT-2204B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBE OIL TEMPERATURE |  | UCP 2101 B | E
|  | PT-2220B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER PRESSURE |  | UCP 2101 B | E
|  | TT-2221B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER TEMPERATURE |  | UCP 2101 B | E
|  | CZSO-2225B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | BARING DEVICE UNLOCK FEED BACK (ON) |  | UCP 2101 B | E
|  | XF-2224B | BK-GCS-HY-120-IN-DW-0006 | 7B of 10 | NO MAIN MOTOR FAULT |  | UCP 2101 B | E
|  | PT-2210B | BK-GCS-HY-120-IN-DW-0006 | 4B of 10 | PRESSURE PACKING N2 PRESSURE |  | UCP 2101 B | E
|  | PT-2211B | BK-GCS-HY-120-IN-DW-0006 | 4B of 10 | ROD PACKING N2 PRESSURE |  | UCP 2101 B | E
|  | LT-2200B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUBE OIL LEVEL |  | UCP 2101 B | E
|  | PSOV-2201B PSOV-2202B PSOV-2203B PSOV-2204B PSOV-2205B | BK-GCS-HY-120-IN-DW-0006 | 2B of 10 | CAPACITY SWITCH ON 0% LOAD (DE ENERGIZED) |  | UCP 2101 B | E
|  | HSS-2125B | BK-GCS-HY-120-IN-DW-0006 | 9B of 10 | CLIENT PERMISSIVE TO START (NOTE 1) |  | UCP 2101 B | E | E
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: A REQUEST PERMISSION SIGNAL (HSS-2126B) FROM UCP WILL BE SENT TO DCS, THEN START PERMISSIOM SIGNAL (HSS-2125B) FROM DCS WILL BE SENT TO UCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 9 از 14
CAUSE AND EFFECT CHARTS LIST

## Control B
CONTROL SIGNALS OF COMPRESSOR B EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C-2101 / C-2102
[7 empty] | EFFECT | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER ON | CRANCK CASE HEATER OFF | AUX. WATER PUMP START | AUX. WATER PUMP STOP | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER START | WATER RESERVOIR HEATER STOP | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR
[7 empty] | TAG NO. | XSS-2202B (Note1) | XSP-2202B | XSS-2203B | XSP-2203B | XSS-2221B | XSP-2221B | XSP-2222B | XSS-2223B | XSP-2223B | PSOV-2201B | PSOV-2202B | PSOV-2203B | PSOV-2204B | PSOV-2205B
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | UCP 2101B | UCP 2101B | UCP 2101B | UCP 2101B | UCP 2101B
|  | TT-2203 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | CRANK CASE LUB OIL TEMPERATURE HIGH | I-30B | UCP 2101B |  |  |  | E
|  | TT-2203 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | CRANK CASE LUB OIL TEMPERATURE LOW | I-30B | UCP 2101B |  |  | E
|  | PT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL PRESSURE HIGH | I-20B | UCP 2101B |  | E
|  | PT-2204 B | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LUB OIL PRESSURE LOW | I-20B | UCP 2101B | E
|  | LT-2213 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER RESERVOIR LEVEL LOW LOW | I-22B | UCP 2101B | [5 empty] | E | E
|  | TT-2213 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER RESERVOIR TEMPERATURE LOW | I-26B | UCP 2101B | [7 empty] | E
|  | TT-2213 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER RESERVOIR TEMPERATURE HIGH | I-26B | UCP 2101B | [8 empty] | E
|  | PT-2220 B | BK-GCS-HY-120-IN-DW-0006 | 5B of 10 | COOLING WATER LINE PRESSURE LOW | I-25B | UCP 2101B |  |  |  |  | E
|  | HSL-2242 B1 | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LOAD 0% SELECTOR SWITCH ON UCP | I-40B | UCP 2101B | [9 empty] | DE | DE | DE | DE | DE
|  | HSL-2242 B2 | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LOAD 25% SELECTOR SWITCH ON UCP | I-40B | UCP 2101B | [9 empty] | E | DE | DE | E | E
|  | HSL-2242 B3 | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LOAD 50% SELECTOR SWITCH ON UCP (NOTE 1) | I-40B | UCP 2101B | [9 empty] | DE | E | DE | E | DE
|  | HSL-2242 B4 | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LOAD 75% SELECTOR SWITCH ON UCP | I-40B | UCP 2101B | [9 empty] | E | E | E | E | E
|  | HSL-2242 B5 | BK-GCS-HY-120-IN-DW-0006 | 3B of 10 | LOAD 100% SELECTOR SWITCH ON UCP | I-40B | UCP 2101B | [9 empty] | E | E | E | E | DE
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER E: ENERGIZE DE: DE-ENERGIZE | [5 empty] | NOTE 1: THE CRANK-END (PSOV-2201 B / 2204 B) AND HEAD-END (PSOV-2202 B / 2203 B) SIDES WILL BE CHANGED ALTERNATELY AS MENTIONED IN CONTROL PHILOSOPHY ("BK-GCS-HY-120-PR-PH-0001").
\
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V03
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 10 از 14
CAUSE AND EFFECT CHARTS LIST

## Messages (hidden)
Oval 931 | Sht 1
Oval 936 | Sht 1
Oval 1656 | Sht 1
Oval 87 | Sht 2
Oval 93 | Sht 2
Oval 94 | Sht 2
Oval 96 | Sht 2
Oval 502 | Sht 2
Oval 102 | Sht 2
Oval 89 | Sht 2
Oval 161 | Sht 4
Oval 525 | Sht 4
Oval 299 | Sht 4
Oval 209 | Sht 4
Rectangle 229 | Sht 4
Oval 241 | Sht 4
Oval 356 | Sht 5
Oval 349 | Sht 5
Oval 350 | Sht 5
Oval 581 | Sht 5
Oval 70 | Sht 11
Oval 71 | Sht 11
Oval 193 | Sht 12
Oval 192 | Sht 12
Oval 206 | Sht 12
Oval 196 | Sht 12
Oval 276 | Sht 13
Oval 277 | Sht 13
Oval 289 | Sht 13
Oval 321 | Sht 14
Oval 326 | Sht 14
Oval 546 | Sht 14
Oval 355 | Sht 14
Oval 358 | Sht 14
Oval 361 | Sht 14
Oval 369 | Sht 14
Oval 363 | Sht 14
Oval 371 | Sht 14
Oval 364 | Sht 14
Oval 372 | Sht 14