## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-LI-0004
Document Title:ALARM AND SET POINT LIST |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-HY-0074 |  |  | Transmital Date:2024/09/30
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-IN-LI-0004_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 03/2294/113124 | 1403/03/24 | حهت اصلاح ستون جدید ایجاد شد.
2 |  |  | 03/2294/113124 | 1403/03/24 | با توجه به حد مجاز مقدار حداقل فشار ورودی آلارم 0.2 صحیح می باشد.
3 |  |  | 03/2294/113124 | 1403/03/24 | موارد لازم اصلاح گردید.
4 |  |  | 03/2294/113124 | 1403/03/24 | موارد لازم اصلاح گردید.
5 |  |  | 03/2294/113124 | 1403/03/24 | موردی در این خصوص در مدرک یافت نشد
6 |  |  | 03/2294/113124 | 1403/03/24 | مغایرتی با استاندارد مشاهده نشد
7 |  |  | 03/2294/113124 | 1403/03/24 | معمولا PSV و PCV در لیست آلارم آورده نمی شود. تجهیزاتی در لیست آورده می شود که به سیستم کنترل متصل می شود. این موارد با کامنت مشاور آورده شده است. SET PINT براساس آخرین p&id لحاظ شده است
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 17 Jul 2023 |  |  |  |  | Date: