## Sheet1
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  |  | INSTRUMENT CABLE LIST | [10 empty] | شماره صفحه: 1 از 11
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 0003 | V06
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT CABLE LIST نگهداشت و افزایش تولید میدان نفتی بینک
V06 |  | Sep.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.SADEGHIAN
V05 |  | Jun.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.SADEGHIAN
V04 |  | Apr.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V03 |  | Feb.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V02 |  | NOV.2023 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V01 |  | OCT.2023 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V00 |  | SEP.2023 |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Sheet2
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  |  | INSTRUMENT CABLE LIST | [12 empty] | شماره صفحه:2 از 11
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI |  | 0003 |  | V06
REVISION RECORD SHEET
Page | V00 | V01 |  | V02 |  | V03 |  | V04 |  |  | Page |  | V05 |  | V06
1 | X | X |  | X |  | X |  | X |  |  | 1 |  | X |  | X
2 | X | X |  | X |  | X |  | X |  |  | 2 |  | X |  | X
3 | X | X |  | X |  | X |  | X |  |  | 3 |  | X |  | X
4 | X | X |  | X |  | X |  | X |  |  | 4 |  | X |  | X
5 | X | X |  | X |  | X |  | X |  |  | 5 |  | X |  | X
6 | X | X |  | X |  | X |  | X |  |  | 6 |  | X |  | X
7 | X | X |  | X |  | X |  | X |  |  | 7 |  | X |  | X
8 | X | X |  | X |  | X |  | X |  |  | 8 |  | X |  | X
9 | [7 empty] | X |  |  | 9 |  | X |  | X
10 | [7 empty] | X |  |  | 10 |  | X |  | X
11 | [7 empty] | X |  |  | 11 |  | X |  | X
12 | [10 empty] | 12
13 | [10 empty] | 13
14 | [10 empty] | 14
15 | [10 empty] | 15
16 | [10 empty] | 16
17 | [10 empty] | 17
18 | [10 empty] | 18
19 | [10 empty] | 19
20 | [10 empty] | 20
21 | [10 empty] | 21
22 | [10 empty] | 22
23 | [10 empty] | 23
24 | [10 empty] | 24
25 | [10 empty] | 25
26 | [10 empty] | 26
27 | [10 empty] | 27
28 | [10 empty] | 28
29 | [10 empty] | 29
30 | [10 empty] | 30
31 | [10 empty] | 31
32 | [10 empty] | 32
33 | [10 empty] | 33
34 | [10 empty] | 34
35 | [10 empty] | 35
36 | [10 empty] | 36
37 | [10 empty] | 37
38 | [10 empty] | 38
39 | [10 empty] | 39
40 | [10 empty] | 40
41 | [10 empty] | 41
42 | [10 empty] | 42
43 | [10 empty] | 43
44 | [10 empty] | 44
45 | [10 empty] | 45
46 | [10 empty] | 46
47 | [10 empty] | 47
48 | [10 empty] | 48
49 | [10 empty] | 49
50 | [10 empty] | 50
51 | [10 empty] | 51
52 | [10 empty] | 52
53 | [10 empty] | 53
54 | [10 empty] | 54
55 | [10 empty] | 55
56 | [10 empty] | 56
57 | [10 empty] | 57
58 | [10 empty] | 58
59 | [10 empty] | 59
60 | [10 empty] | 60
61 | [10 empty] | 61
62 | [10 empty] | 62
63 | [10 empty] | 63
64 | [10 empty] | 64

## CompA
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V06
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201A | JBU-S-2101A | C-PSOV-2201A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
2 | IC-C-PSOV-2202A |  | C-PSOV-2202A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
3 | IC-C-PSOV-2203A |  | C-PSOV-2203A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
4 | IC-C-PSOV-2204A |  | C-PSOV-2204A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
5 | IC-C-PSOV-2205A |  | C-PSOV-2205A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
6 | MC-JBU-S-2101A | UCP-2101A | JBU-S-2101A |  | 7x2x2.5mm^3 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-C-TS-2191A | C-TS-2191A | JBU-D-2101A |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
8 | IC-C-TS-2194A | C-TS-2194A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
9 | IC-C-PS-2133A | C-PS-2133A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
10 | IC-C-PS-2204A | C-PS-2204A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
11 | IC-C-PS-2220A | C-PS-2220A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
12 | MC-JBU-D-2101A | JBU-D-2101A | UCP-2101A |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
13 | IC-FT-2121A | FT-2121A | JBU-A-2101 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
14 | IC-TT-2122A | TT-2122A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
15 | IC-PDT-2122A | PDT-2122A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
16 | IC-PT-2123A | PT-2123A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
17 | IC-TT-2123A | TT-2123A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
18 | IC-PT-2124A | PT-2124A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
19 | IC-FT-2131A | FT-2131A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
20 | IC-TT-2132A | TT-2132A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
21 | IC-PT-2132A | PT-2132A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
22 | IC-PDT-2132A | PDT-2132A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
23 | IC-TT-2133A | TT-2133A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
24 | IC-PT-2133A | PT-2133A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
25 | IC-PCVY-2123A | PCVY-2123A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
26 | IC-PCYZ-2123A | PCYZ-2123A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
27 | MC-JBU-A-2101 | JBU-A-2101 | UCP-2101A |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
28 | IC-C-TE-2214A | C-TE-2214A | C-TT-2214A |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
29 | IC-C-TE-2215A | C-TE-2215A | C-TT-2215A |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
30 | IC-C-TE-2216A | C-TE-2216A | C-TT-2216A |  | 1x3x1.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | Blue | 10 | M20 | IS | Supply by Havayar
31 | IC-C-TE-2217A | C-TE-2217A | C-TT-22117A | TT-22117A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
32 | IC-C-TE-2218A | C-TE-2218A | C-TT-2218A | TT-2218A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
33 | IC-C-TE-2219A | C-TE-2219A | C-TT-2219A | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
34 | IC-C-TE-2220A | C-TE-2220A | C-TT-2220A | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | _ | M20 | N/A | Supply by Havayar
35 | IC-C-TT-2203A | C-TT-2203A | JBU-A-2101A |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
36 | IC-C-TT-2213A | C-TT-2213A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
37 | IC-C-PT-2204A | C-PT-2204A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
38 | IC-C-PT-2220A | C-PT-2220A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
39 | IC-C-LT-2213A | C-LT-2213A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
40 | IC-C-TT-2191A | C-TT-2191A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
41 | IC-C-TT-2194A | C-TT-2194A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
42 | IC-C-PT-2201A | C-PT-2201A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
43 | IC-C-PT-2210A | C-PT-2210A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
44 | IC-C-PT-2211A | C-PT-2211A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
45 | IC-C-PT-2212A | C-PT-2212A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
46 | IC-C-PT-2200A | C-PT-2200A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
47 | IC-C-LT-2200A | C-LT-2200A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
48 | IC-C-FT-2206A | C-FT-2206A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
49 | IC-C-TT-2204A | C-TT-2204A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
50 | IC-C-PDT-2204A | C-PDT-2204A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
51 | MC-JBU-A-2101A | JBU-A-2101A | UCP-2101A |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
52 | IC-C-ZT-2200A | C-ZT-2200A | JBU-A-2102A |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
53 | IC-C-ZT-2201A | C-ZT-2201A |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
54 | IC-C-XT-2200A | C-XT-2200A |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8.5 | M20 | N/A | Supply by Havayar
55 | MC-JBU-A-2102A | JBU-A-2102A | UCP-2101A |  | 7x3x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M40 | IS | Out of Havayar scope of work (By Hirgan)
56 | IC-C-TT-2214A | C-TT-2214A | JBU-A-2103A |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing DE
57 | IC-C-TT-2215A | C-TT-2215A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing NDE
58 | IC-C-TT-2216A | C-TT-2216A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
59 | IC-C-TT-2217A | C-TT-2217A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
60 | IC-C-TT-2218A | C-TT-2218A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
61 | IC-C-TT-2219A | C-TT-2219A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
62 | IC-C-TT-2220A | C-TT-2220A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
63 | IC-C-TT-2221A | C-TT-2221A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 20 | M20 | IS | Supply by Havayar
64 | IC-C-VT-2200A | C-VT-2200A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
65 | IC-C-VT-2201A | C-VT-2201A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
66 | IC-C-VT-2202A | C-VT-2202A |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
67 | MC-JBU-A-2103A | JBU-A-2103A | UCP-2101A |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
68 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101A |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
69 | MC-LCP-2101A1 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
70 | MC-LCP-2101A2 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
71 | MC-LCP-2101A3 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
72 | MC-LCP-2101A4 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
73 | MC-LCP-2101A5 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
74 | MC-LCP-2101A6 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 3x2.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M25 | NIS | Out of Havayar scope of work (By Hirgan)
75 | `MC-MCC-2101A1 | Client IRP | UCP-2101A OIL HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
76 |  |  | UCP-2101A OIL HEATER Stop Command | 40-JB-DIA-351
77 |  |  | UCP-2101A OIL HEATER Start Command | 40-JB-DIA-351
78 |  |  | UCP-2101A OIL HEATER Running Status | 40-JB-DIA-351
79 |  |  | UCP-2101A OIL HEATER Fault Status | 40-JB-DIA-351
80 | `MC-MCC-2101A2 | Client IRP | UCP-2101A AUX OIL PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
81 |  |  | UCP-2101A AUX OIL PUMP Stop Command | 40-JB-DIA-351
82 |  |  | UCP-2101A AUX OIL PUMP Start Command | 40-JB-DIA-351
83 |  |  | UCP-2101A AUX OIL PUMP Running Status | 40-JB-DIA-351
84 |  |  | UCP-2101A AUX OIL PUMP Fault Status | 40-JB-DIA-351
85 | `MC-MCC-2101A3 | Client IRP | UCP-2101A LUBRICATOR HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
86 |  |  | UCP-2101A LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
87 |  |  | UCP-2101A LUBRICATOR HEATER Start Command | 40-JB-DIA-351
88 |  |  | UCP-2101A LUBRICATOR HEATER Running Status | 40-JB-DIA-351
89 |  |  | UCP-2101A LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
90 | `MC-MCC-2101A4 | Client IRP | UCP-2101A LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
91 |  |  | UCP-2101A LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351
92 |  |  | UCP-2101A LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
93 |  |  | UCP-2101A LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
94 |  |  | UCP-2101A LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
95 | `MC-MCC-2101A5 | Client IRP | UCP-2101A MAIN MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
96 |  |  | UCP-2101A MAIN MOTOR Stop Command | 40-JB-DIA-351
97 |  |  | UCP-2101A MAIN MOTOR Start Command | 40-JB-DIA-351
98 |  |  | UCP-2101A MAIN MOTOR Running Status | 40-JB-DIA-351
99 |  |  | UCP-2101A MAIN MOTOR Fault Status | 40-JB-DIA-351
100 | `MC-MCC-2101A6 | Client IRP | UCP-2101A OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
101 |  |  | UCP-2101A OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101A OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101A OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101A OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101A7 | Client IRP | UCP-2101A MAIN WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
106 |  |  | UCP-2101A MAIN WATER PUMP Stop Command | 40-JB-DIA-351
107 |  |  | UCP-2101A MAIN WATER PUMP Start Command | 40-JB-DIA-351
108 |  |  | UCP-2101A MAIN WATER PUMP Running Status | 40-JB-DIA-351
109 |  |  | UCP-2101A MAIN WATER PUMP Fault Status | 40-JB-DIA-351
110 | `MC-MCC-2101A8 | Client IRP | UCP-2101A AUX WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
111 |  |  | UCP-2101A AUX WATER PUMP Stop Command | 40-JB-DIA-351
112 |  |  | UCP-2101A AUX WATER PUMP Start Command | 40-JB-DIA-351
113 |  |  | UCP-2101A AUX WATER PUMP Running Status | 40-JB-DIA-351
114 |  |  | UCP-2101A AUX WATER PUMP Fault Status | 40-JB-DIA-351
115 | `MC-MCC-2101A9 | Client IRP | UCP-2101A WATER HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
116 |  |  | UCP-2101A WATER HEATER Stop Command | 40-JB-DIA-351
117 |  |  | UCP-2101A WATER HEATER Start Command | 40-JB-DIA-351
118 |  |  | UCP-2101A WATER HEATER Running Status | 40-JB-DIA-351
119 |  |  | UCP-2101A WATER HEATER Fault Status | 40-JB-DIA-351
120 | `MC-MCC-2101A10 | Client IRP | UCP-2101A WATER COOLER A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
121 |  |  | UCP-2101A WATER COOLER A Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101A WATER COOLER A Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101A WATER COOLER A Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101A WATER COOLER A Fault Status | 40-JB-DIA-351
125 | `MC-MCC-2101A11 | Client IRP | UCP-2101A BARRING MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
126 |  |  | UCP-2101A BARRING MOTOR Stop Command | 40-JB-DIA-351
127 |  |  | UCP-2101A BARRING MOTOR Start Command | 40-JB-DIA-351
128 |  |  | UCP-2101A BARRING MOTOR Running Status | 40-JB-DIA-351
129 |  |  | UCP-2101A BARRING MOTOR Fault Status | 40-JB-DIA-351
130 | `MC-MCC-2101A12 | Client IRP | UCP-2101A OIL COOLER MOTOR B | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
131 |  |  | UCP-2101A OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
132 |  |  | UCP-2101A OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
133 |  |  | UCP-2101A OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
134 |  |  | UCP-2101A OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
135 | MC-ESD-2101A | ESD | UCP-2101A | 40-JB-DIA-351 | 7x2x1mm^2 | CU,PVC,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
136 | MC-DCS-2101A | DCS | UCP-2101A | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
137 | IC-PT-2121A | DCS | UCP-2101A | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M20 | NIS | Out of Havayar scope of work (By Hirgan) Spill Back
138 | IC-C-VS-2205A | C-VS-2205A | JBU-D-2102A |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
139 | IC-C-VS-2206A | C-VS-2206A |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
140 | IC-C-VS-2207A | C-VS-2207A |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
141 | MC-JBU-D-2102A | JBU-D-2102A | UCP-2101A |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FLAME RETARDANT |  |  | Gray | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)

## CompB
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V06
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201B | JBU-S-2101B | C-PSOV-2201B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
2 | IC-C-PSOV-2202B |  | C-PSOV-2202B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
3 | IC-C-PSOV-2203B |  | C-PSOV-2203B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
4 | IC-C-PSOV-2204B |  | C-PSOV-2204B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
5 | IC-C-PSOV-2205B |  | C-PSOV-2205B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
6 | MC-JBU-S-2101B | UCP-2101B | JBU-S-2101B |  | 7x2x2.5mm^3 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-C-TS-2191B | C-TS-2191B | JBU-D-2101B |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
8 | IC-C-TS-2194B | C-TS-2194B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
9 | IC-C-PS-2133B | C-PS-2133B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
10 | IC-C-PS-2204B | C-PS-2204B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
11 | IC-C-PS-2220B | C-PS-2220B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
12 | MC-JBU-D-2101B | JBU-D-2101B | UCP-2101B |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
13 | IC-FT-2121B | FT-2121B | JBU-A-2102 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
14 | IC-TT-2122B | TT-2122B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
15 | IC-PDT-2122B | PDT-2122B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
16 | IC-PT-2123B | PT-2123B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
17 | IC-TT-2123B | TT-2123B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
18 | IC-PT-2124B | PT-2124B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
19 | IC-FT-2131B | FT-2131B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
20 | IC-TT-2132B | TT-2132B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
21 | IC-PT-2132B | PT-2132B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
22 | IC-PDT-2132B | PDT-2132B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
23 | IC-TT-2133B | TT-2133B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
24 | IC-PT-2133B | PT-2133B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
25 | IC-PCVY-2123B | PCVY-2123B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
26 | IC-PCYZ-2123B | PCYZ-2123B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
27 | MC-JBU-A-2102 | JBU-A-2102 | UCP-2101B |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
28 | IC-C-TE-2214B | C-TE-2214B | C-TT-2214B |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
29 | IC-C-TE-2215B | C-TE-2215B | C-TT-2215B |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
30 | IC-C-TE-2216B | C-TE-2216B | C-TT-2216B |  | 1x3x1.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | Blue | 10 | M20 | IS | Supply by Havayar
31 | IC-C-TE-2217B | C-TE-2217B | C-TT-22117B | TT-22117A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
32 | IC-C-TE-2218B | C-TE-2218B | C-TT-2218B | TT-2218A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
33 | IC-C-TE-2219B | C-TE-2219B | C-TT-2219B | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
34 | IC-C-TE-2220B | C-TE-2220B | C-TT-2220B | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | _ | M20 | N/A | Supply by Havayar
35 | IC-C-TT-2203B | C-TT-2203B | JBU-A-2101B |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
36 | IC-C-TT-2213B | C-TT-2213B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
37 | IC-C-PT-2204B | C-PT-2204B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
38 | IC-C-PT-2220B | C-PT-2220B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
39 | IC-C-LT-2213B | C-LT-2213B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
40 | IC-C-TT-2191B | C-TT-2191B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
41 | IC-C-TT-2194B | C-TT-2194B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
42 | IC-C-PT-2201B | C-PT-2201B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
43 | IC-C-PT-2210B | C-PT-2210B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
44 | IC-C-PT-2211B | C-PT-2211B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
45 | IC-C-PT-2212B | C-PT-2212B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
46 | IC-C-PT-2200B | C-PT-2200B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
47 | IC-C-LT-2200B | C-LT-2200B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
48 | IC-C-FT-2206B | C-FT-2206B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
49 | IC-C-TT-2204B | C-TT-2204B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
50 | IC-C-PDT-2204B | C-PDT-2204B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
51 | MC-JBU-A-2101B | JBU-A-2101B | UCP-2101B |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
52 | IC-C-ZT-2200B | C-ZT-2200B | JBU-A-2102B |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
53 | IC-C-ZT-2201B | C-ZT-2201B |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
54 | IC-C-XT-2200B | C-XT-2200B |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8.5 | M20 | N/A | Supply by Havayar
55 | MC-JBU-A-2102B | JBU-A-2102B | UCP-2101B |  | 7x3x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M40 | IS | Out of Havayar scope of work (By Hirgan)
56 | IC-C-TT-2214B | C-TT-2214B | JBU-A-2103B |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing DE
57 | IC-C-TT-2215B | C-TT-2215B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing NDE
58 | IC-C-TT-2216B | C-TT-2216B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
59 | IC-C-TT-2217B | C-TT-2217B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
60 | IC-C-TT-2218B | C-TT-2218B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
61 | IC-C-TT-2219B | C-TT-2219B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
62 | IC-C-TT-2220B | C-TT-2220B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
63 | IC-C-TT-2221B | C-TT-2221B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 20 | M20 | IS | Supply by Havayar
64 | IC-C-VT-2200B | C-VT-2200B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
65 | IC-C-VT-2201B | C-VT-2201B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
66 | IC-C-VT-2202B | C-VT-2202B |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
67 | MC-JBU-A-2103B | JBU-A-2103B | UCP-2101B |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
68 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101B |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
69 | MC-LCP-2101B1 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
70 | MC-LCP-2101B2 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
71 | MC-LCP-2101B3 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
72 | MC-LCP-2101B4 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
73 | MC-LCP-2101B5 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
74 | MC-LCP-2101B6 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 3x2.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M25 | NIS | Out of Havayar scope of work (By Hirgan)
75 | `MC-MCC-2101B1 | Client IRP | UCP-2101B OIL HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
76 |  |  | UCP-2101B OIL HEATER Stop Command | 40-JB-DIA-351
77 |  |  | UCP-2101B OIL HEATER Start Command | 40-JB-DIA-351
78 |  |  | UCP-2101B OIL HEATER Running Status | 40-JB-DIA-351
79 |  |  | UCP-2101B OIL HEATER Fault Status | 40-JB-DIA-351
80 | `MC-MCC-2101B2 | Client IRP | UCP-2101B AUX OIL PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
81 |  |  | UCP-2101B AUX OIL PUMP Stop Command | 40-JB-DIA-351
82 |  |  | UCP-2101B AUX OIL PUMP Start Command | 40-JB-DIA-351
83 |  |  | UCP-2101B AUX OIL PUMP Running Status | 40-JB-DIA-351
84 |  |  | UCP-2101B AUX OIL PUMP Fault Status | 40-JB-DIA-351
85 | `MC-MCC-2101B3 | Client IRP | UCP-2101B LUBRICATOR HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
86 |  |  | UCP-2101B LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
87 |  |  | UCP-2101B LUBRICATOR HEATER Start Command | 40-JB-DIA-351
88 |  |  | UCP-2101B LUBRICATOR HEATER Running Status | 40-JB-DIA-351
89 |  |  | UCP-2101B LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
90 | `MC-MCC-2101B4 | Client IRP | UCP-2101B LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
91 |  |  | UCP-2101B LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351
92 |  |  | UCP-2101B LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
93 |  |  | UCP-2101B LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
94 |  |  | UCP-2101B LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
95 | `MC-MCC-2101B5 | Client IRP | UCP-2101B MAIN MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
96 |  |  | UCP-2101B MAIN MOTOR Stop Command | 40-JB-DIA-351
97 |  |  | UCP-2101B MAIN MOTOR Start Command | 40-JB-DIA-351
98 |  |  | UCP-2101B MAIN MOTOR Running Status | 40-JB-DIA-351
99 |  |  | UCP-2101B MAIN MOTOR Fault Status | 40-JB-DIA-351
100 | `MC-MCC-2101B6 | Client IRP | UCP-2101B OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
101 |  |  | UCP-2101B OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101B OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101B OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101B OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101B7 | Client IRP | UCP-2101B MAIN WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
106 |  |  | UCP-2101B MAIN WATER PUMP Stop Command | 40-JB-DIA-351
107 |  |  | UCP-2101B MAIN WATER PUMP Start Command | 40-JB-DIA-351
108 |  |  | UCP-2101B MAIN WATER PUMP Running Status | 40-JB-DIA-351
109 |  |  | UCP-2101B MAIN WATER PUMP Fault Status | 40-JB-DIA-351
110 | `MC-MCC-2101B8 | Client IRP | UCP-2101B AUX WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
111 |  |  | UCP-2101B AUX WATER PUMP Stop Command | 40-JB-DIA-351
112 |  |  | UCP-2101B AUX WATER PUMP Start Command | 40-JB-DIA-351
113 |  |  | UCP-2101B AUX WATER PUMP Running Status | 40-JB-DIA-351
114 |  |  | UCP-2101B AUX WATER PUMP Fault Status | 40-JB-DIA-351
115 | `MC-MCC-2101B9 | Client IRP | UCP-2101B WATER HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
116 |  |  | UCP-2101B WATER HEATER Stop Command | 40-JB-DIA-351
117 |  |  | UCP-2101B WATER HEATER Start Command | 40-JB-DIA-351
118 |  |  | UCP-2101B WATER HEATER Running Status | 40-JB-DIA-351
119 |  |  | UCP-2101B WATER HEATER Fault Status | 40-JB-DIA-351
120 | `MC-MCC-2101B10 | Client IRP | UCP-2101B WATER COOLER A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
121 |  |  | UCP-2101B WATER COOLER A Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101B WATER COOLER A Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101B WATER COOLER A Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101B WATER COOLER A Fault Status | 40-JB-DIA-351
125 | `MC-MCC-2101B11 | Client IRP | UCP-2101B BARRING MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
126 |  |  | UCP-2101B BARRING MOTOR Stop Command | 40-JB-DIA-351
127 |  |  | UCP-2101B BARRING MOTOR Start Command | 40-JB-DIA-351
128 |  |  | UCP-2101B BARRING MOTOR Running Status | 40-JB-DIA-351
129 |  |  | UCP-2101B BARRING MOTOR Fault Status | 40-JB-DIA-351
130 | `MC-MCC-2101B12 | Client IRP | UCP-2101B OIL COOLER MOTOR B | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
131 |  |  | UCP-2101B OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
132 |  |  | UCP-2101B OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
133 |  |  | UCP-2101B OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
134 |  |  | UCP-2101B OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
135 | MC-ESD-2101B | ESD | UCP-2101B | 40-JB-DIA-351 | 7x2x1mm^2 | CU,PVC,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
136 | MC-DCS-2101B | DCS | UCP-2101B | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
137 | IC-PT-2121B | DCS | UCP-2101B | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M20 | NIS | Out of Havayar scope of work (By Hirgan) Spill Back
138 | IC-C-VS-2205B | C-VS-2205B | JBU-D-2102B |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
139 | IC-C-VS-2206B | C-VS-2206B |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
140 | IC-C-VS-2207B | C-VS-2207B |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
141 | MC-JBU-D-2102B | JBU-D-2102B | UCP-2101B |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FLAME RETARDANT |  |  | Gray | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)

## CompC
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V06
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201C | JBU-S-2101C | C-PSOV-2201C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
2 | IC-C-PSOV-2202C |  | C-PSOV-2202C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
3 | IC-C-PSOV-2203C |  | C-PSOV-2203C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
4 | IC-C-PSOV-2204C |  | C-PSOV-2204C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
5 | IC-C-PSOV-2205C |  | C-PSOV-2205C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
6 | MC-JBU-S-2101C | UCP-2101C | JBU-S-2101C |  | 7x2x2.5mm^3 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-C-TS-2191C | C-TS-2191C | JBU-D-2101C |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
8 | IC-C-TS-2194C | C-TS-2194C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
9 | IC-C-PS-2133C | C-PS-2133C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
10 | IC-C-PS-2204C | C-PS-2204C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
11 | IC-C-PS-2220C | C-PS-2220C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20 | NIS | Supply by Havayar
12 | MC-JBU-D-2101C | JBU-D-2101C | UCP-2101C |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
13 | IC-FT-2121C | FT-2121C | JBU-A-2103 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
14 | IC-TT-2122C | TT-2122C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
15 | IC-PDT-2122C | PDT-2122C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
16 | IC-PT-2123C | PT-2123C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
17 | IC-TT-2123C | TT-2123C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
18 | IC-PT-2124C | PT-2124C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
19 | IC-FT-2131C | FT-2131C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
20 | IC-TT-2132C | TT-2132C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
21 | IC-PT-2132C | PT-2132C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
22 | IC-PDT-2132C | PDT-2132C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
23 | IC-TT-2133C | TT-2133C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
24 | IC-PT-2133C | PT-2133C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
25 | IC-PCVY-2123C | PCVY-2123C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
26 | IC-PCYZ-2123C | PCYZ-2123C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar Loose item
27 | MC-JBU-A-2103 | JBU-A-2103 | UCP-2101C |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
28 | IC-C-TE-2214C | C-TE-2214C | C-TT-2214C |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
29 | IC-C-TE-2215C | C-TE-2215C | C-TT-2215C |  | 1x3x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
30 | IC-C-TE-2216C | C-TE-2216C | C-TT-2216C |  | 1x3x1.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | Blue | 10 | M20 | IS | Supply by Havayar
31 | IC-C-TE-2217C | C-TE-2217C | C-TT-22117C | TT-22117A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
32 | IC-C-TE-2218C | C-TE-2218C | C-TT-2218C | TT-2218A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
33 | IC-C-TE-2219C | C-TE-2219C | C-TT-2219C | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | 10 | M20 | N/A | Supply by Havayar
34 | IC-C-TE-2220C | C-TE-2220C | C-TT-2220C | TT-2219A | 1x3x0.5mm^2 | Special Cable-RTD cable 3x0.5mm^2 |  |  | N/A | _ | M20 | N/A | Supply by Havayar
35 | IC-C-TT-2203C | C-TT-2203C | JBU-A-2101C |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
36 | IC-C-TT-2213C | C-TT-2213C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
37 | IC-C-PT-2204C | C-PT-2204C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
38 | IC-C-PT-2220C | C-PT-2220C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
39 | IC-C-LT-2213C | C-LT-2213C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
40 | IC-C-TT-2191C | C-TT-2191C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
41 | IC-C-TT-2194C | C-TT-2194C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
42 | IC-C-PT-2201C | C-PT-2201C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
43 | IC-C-PT-2210C | C-PT-2210C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
44 | IC-C-PT-2211C | C-PT-2211C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
45 | IC-C-PT-2212C | C-PT-2212C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
46 | IC-C-PT-2200C | C-PT-2200C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
47 | IC-C-LT-2200C | C-LT-2200C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 10 | M20 | IS | Supply by Havayar
48 | IC-C-FT-2206C | C-FT-2206C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
49 | IC-C-TT-2204C | C-TT-2204C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
50 | IC-C-PDT-2204C | C-PDT-2204C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | 20 | M20 | IS | Supply by Havayar
51 | MC-JBU-A-2101C | JBU-A-2101C | UCP-2101C |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
52 | IC-C-ZT-2200C | C-ZT-2200C | JBU-A-2102C |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
53 | IC-C-ZT-2201C | C-ZT-2201C |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8 | M20 | N/A | Supply by Havayar
54 | IC-C-XT-2200C | C-XT-2200C |  |  | Special cable | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | N/A | 8.5 | M20 | N/A | Supply by Havayar
55 | MC-JBU-A-2102C | JBU-A-2102C | UCP-2101C |  | 7x3x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Blue | _ | M40 | IS | Out of Havayar scope of work (By Hirgan)
56 | IC-C-TT-2214C | C-TT-2214C | JBU-A-2103C |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing DE
57 | IC-C-TT-2215C | C-TT-2215C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar Bearing NDE
58 | IC-C-TT-2216C | C-TT-2216C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
59 | IC-C-TT-2217C | C-TT-2217C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
60 | IC-C-TT-2218C | C-TT-2218C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
61 | IC-C-TT-2219C | C-TT-2219C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
62 | IC-C-TT-2220C | C-TT-2220C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
63 | IC-C-TT-2221C | C-TT-2221C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 20 | M20 | IS | Supply by Havayar
64 | IC-C-VT-2200C | C-VT-2200C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
65 | IC-C-VT-2201C | C-VT-2201C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
66 | IC-C-VT-2202C | C-VT-2202C |  |  | 1x2x1.5mm^2 | CU,PVC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | 10 | M20 | IS | Supply by Havayar
67 | MC-JBU-A-2103C | JBU-A-2103C | UCP-2101C |  | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FIRE RESISTANT |  |  | Blue Red Strip | _ | M50 | IS | Out of Havayar scope of work (By Hirgan)
68 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101C |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
69 | MC-LCP-2101C1 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
70 | MC-LCP-2101C2 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
71 | MC-LCP-2101C3 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
72 | MC-LCP-2101C4 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan)
73 | MC-LCP-2101C5 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
74 | MC-LCP-2101C6 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 3x2.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | _ | M25 | NIS | Out of Havayar scope of work (By Hirgan)
75 | `MC-MCC-2101C1 | Client IRP | UCP-2101C OIL HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
76 |  |  | UCP-2101C OIL HEATER Stop Command | 40-JB-DIA-351
77 |  |  | UCP-2101C OIL HEATER Start Command | 40-JB-DIA-351
78 |  |  | UCP-2101C OIL HEATER Running Status | 40-JB-DIA-351
79 |  |  | UCP-2101C OIL HEATER Fault Status | 40-JB-DIA-351
80 | `MC-MCC-2101C2 | Client IRP | UCP-2101C AUX OIL PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
81 |  |  | UCP-2101C AUX OIL PUMP Stop Command | 40-JB-DIA-351
82 |  |  | UCP-2101C AUX OIL PUMP Start Command | 40-JB-DIA-351
83 |  |  | UCP-2101C AUX OIL PUMP Running Status | 40-JB-DIA-351
84 |  |  | UCP-2101C AUX OIL PUMP Fault Status | 40-JB-DIA-351
85 | `MC-MCC-2101C3 | Client IRP | UCP-2101C LUBRICATOR HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
86 |  |  | UCP-2101C LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
87 |  |  | UCP-2101C LUBRICATOR HEATER Start Command | 40-JB-DIA-351
88 |  |  | UCP-2101C LUBRICATOR HEATER Running Status | 40-JB-DIA-351
89 |  |  | UCP-2101C LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
90 | `MC-MCC-2101C4 | Client IRP | UCP-2101C LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
91 |  |  | UCP-2101C LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351
92 |  |  | UCP-2101C LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
93 |  |  | UCP-2101C LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
94 |  |  | UCP-2101C LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
95 | `MC-MCC-2101C5 | Client IRP | UCP-2101C MAIN MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
96 |  |  | UCP-2101C MAIN MOTOR Stop Command | 40-JB-DIA-351
97 |  |  | UCP-2101C MAIN MOTOR Start Command | 40-JB-DIA-351
98 |  |  | UCP-2101C MAIN MOTOR Running Status | 40-JB-DIA-351
99 |  |  | UCP-2101C MAIN MOTOR Fault Status | 40-JB-DIA-351
100 | `MC-MCC-2101C6 | Client IRP | UCP-2101C OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
101 |  |  | UCP-2101C OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101C OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101C OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101C OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101C7 | Client IRP | UCP-2101C MAIN WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
106 |  |  | UCP-2101C MAIN WATER PUMP Stop Command | 40-JB-DIA-351
107 |  |  | UCP-2101C MAIN WATER PUMP Start Command | 40-JB-DIA-351
108 |  |  | UCP-2101C MAIN WATER PUMP Running Status | 40-JB-DIA-351
109 |  |  | UCP-2101C MAIN WATER PUMP Fault Status | 40-JB-DIA-351
110 | `MC-MCC-2101C8 | Client IRP | UCP-2101C AUX WATER PUMP ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
111 |  |  | UCP-2101C AUX WATER PUMP Stop Command | 40-JB-DIA-351
112 |  |  | UCP-2101C AUX WATER PUMP Start Command | 40-JB-DIA-351
113 |  |  | UCP-2101C AUX WATER PUMP Running Status | 40-JB-DIA-351
114 |  |  | UCP-2101C AUX WATER PUMP Fault Status | 40-JB-DIA-351
115 | `MC-MCC-2101C9 | Client IRP | UCP-2101C WATER HEATER ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
116 |  |  | UCP-2101C WATER HEATER Stop Command | 40-JB-DIA-351
117 |  |  | UCP-2101C WATER HEATER Start Command | 40-JB-DIA-351
118 |  |  | UCP-2101C WATER HEATER Running Status | 40-JB-DIA-351
119 |  |  | UCP-2101C WATER HEATER Fault Status | 40-JB-DIA-351
120 | `MC-MCC-2101C10 | Client IRP | UCP-2101C WATER COOLER A ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
121 |  |  | UCP-2101C WATER COOLER A Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101C WATER COOLER A Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101C WATER COOLER A Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101C WATER COOLER A Fault Status | 40-JB-DIA-351
125 | `MC-MCC-2101C11 | Client IRP | UCP-2101C BARRING MOTOR ESD Command | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
126 |  |  | UCP-2101C BARRING MOTOR Stop Command | 40-JB-DIA-351
127 |  |  | UCP-2101C BARRING MOTOR Start Command | 40-JB-DIA-351
128 |  |  | UCP-2101C BARRING MOTOR Running Status | 40-JB-DIA-351
129 |  |  | UCP-2101C BARRING MOTOR Fault Status | 40-JB-DIA-351
130 | `MC-MCC-2101C12 | Client IRP | UCP-2101C OIL COOLER MOTOR B | 40-JB-DIA-351 | 12core X 2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M25 | NIS | Out of Havayar scope of work ( (By Hirgan Electrical Dep )
131 |  |  | UCP-2101C OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
132 |  |  | UCP-2101C OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
133 |  |  | UCP-2101C OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
134 |  |  | UCP-2101C OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
135 | MC-ESD-2101C | ESD | UCP-2101C | 40-JB-DIA-351 | 7x2x1mm^2 | CU,PVC,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)
136 | MC-DCS-2101C | DCS | UCP-2101C | 40-JB-DIA-351 | 12x2x1mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
137 | IC-PT-2121C | DCS | UCP-2101C | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,PVC,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M20 | NIS | Out of Havayar scope of work (By Hirgan) Spill Back
138 | IC-C-VS-2205C | C-VS-2205C | JBU-D-2102C |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
139 | IC-C-VS-2206C | C-VS-2206C |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
140 | IC-C-VS-2207C | C-VS-2207C |  |  | 1x2x2.5mm^2 | CU,PVC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Gray | 10 | M20 | NIS | Supply by Havayar
141 | MC-JBU-D-2102C | JBU-D-2102C | UCP-2101C |  | 7x2x1mm^2 | CU,PVC,SC,OSC,SWA,PVC,,FLAME RETARDANT |  |  | Gray | _ | M32 | NIS | Out of Havayar scope of work (By Hirgan)