## PAGE 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
ELECTRICAL/UPS CONSUMPTION LOAD LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادر کننده | تسهیلات | رشته | رشته | نوع مدرک | سریال | نسخه | نسخه | شماره صفحه : 1 از 4
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 | XX | EL | LI | 0001 | DXX | V01
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL/UPS CONSUMPTION LOAD LIST نگهداشت و افزایش تولید میدان نفتی بینک
V01 |  | Oct.2024 |  | IFR |  | Havayar Co. |  |  |  | M.Fakharian |  |  |  | M.SADEGHIAN
V00 |  | JUN.2023 |  | IFR |  | Havayar Co. |  |  |  | M.Fakharian |  |  |  | A.M.MoHSENI
Rev. |  | Date |  | Purpose of Issue / Status |  | Prepared by: |  |  |  | Checked by: |  |  |  | Approved by: | CLIENT Approval
Class:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
ELECTRICAL/UPS CONSUMPTION LOAD LIST
شماره پیمان: |  |  |  | پروژه |  |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته | نوع مدرک | سریال | نسخه | شمار0 صفحه : 2 از 4
9184 – 073 - 053 |  |  |  | BK |  |  | GCS |  | HY |  | 120 |  |  | EL | LI | 0001 | V01
REVISION RECORD SHEET
Page |  | V00 | V01 |  | V02 |  | V03 | V04 |  | V05 |  | V06 | Page | V00 | V01 | V02 | V03 |  | V04 | V05 | V06
1 | X | X | X | [9 empty] | 40
2 | X | X | X | [9 empty] | 41
3 | X | X | X | [9 empty] | 42
4 | X | X | X | [9 empty] | 43
5 | X | [11 empty] | 44
6 | X | [11 empty] | 45
7 | X | [11 empty] | 46
8 | X | [11 empty] | 47
9 | X | [11 empty] | 48
10 | X | [11 empty] | 49
11 | X | [11 empty] | 50
12 | X | [11 empty] | 51
13 | X | [11 empty] | 52
14 | X | [11 empty] | 53
15 | X | [11 empty] | 54
16 | X | [11 empty] | 55
17 | X | [11 empty] | 56
18 | X | [11 empty] | 57
19 | X | [11 empty] | 58
20 | X | [11 empty] | 59
21 | X | [11 empty] | 60
22 | X | [11 empty] | 61
23 | X | [11 empty] | 62
24 | X | [11 empty] | 63
25 | X |  |  |  |  | 66 | [6 empty] | 64
26 | X |  |  |  |  | 67 | [6 empty] | 65
27 | X |  |  |  |  | 68 | [6 empty] | 66
28 | X |  |  |  |  | 69 | [6 empty] | 67
29 | X |  |  |  |  | 70 | [6 empty] | 68
30 | X |  |  |  |  | 71 | [6 empty] | 69
31 | X |  |  |  |  | 72 | [6 empty] | 70
32 | X |  |  |  |  | 73 | [6 empty] | 71
33 | X |  |  |  |  | 74 | [6 empty] | 72
34 | X |  |  |  |  | 75 | [6 empty] | 73
35 | X |  |  |  |  | 76 | [6 empty] | 74
36 | X |  |  |  |  | 77 | [6 empty] | 75
37 | X |  |  |  |  | 78 | [6 empty] | 76
38 | X |  |  |  |  | 79 | [6 empty] | 77
39 | X |  |  |  |  | 80 | [6 empty] | 78

## PAGE 3&4
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
ELECTRICAL/UPS CONSUMPTION LOAD LIST
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه : 3 از 4
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | HY |  | 120 |  | EL | LI | 0001 | V01
No. | DESCRIPTION |  |  |  | RATED VOLTAGE (V) | SUPPLY FEEDER | NO. OF PHASE | Feeder Type Motorized | FREQUENCY (HZ) | STARTING TYPE Starting panel By client | Continuous/ Intermittent | RATED POWER (KW) |  | QUANTITY | TOTAL RATED POWER (KW) (equipment consumption) |  | Number of feeder from client panel
1 | Compressor # C-2101-C1 A # C-2102-C2 A | Main Motor |  |  | 11000 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 1070 |  | 1 | 1070 |  | 1
|  | Space Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1 |  | 1 | 1 |  | 1
|  | Oil Heater # H-2101-LH A |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1.5 |  | 1 | 1.5 |  | 1
|  | Barring Device Motor # C-2101-BM A |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Intermittent | 2.2 |  | 1 | 2.2 |  | 1
|  | Electrical Heat Tracing (Part of HAVAYAR Scope ) |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 2 |  | 1 | 2 |  | 1
|  | Aux. Oil Pump Motor # M-2101-AP A |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 5.5 |  | 1 | 5.5 |  | 1
|  | Lube. Oil Cooler # AE-2101-OC A |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 3 |  | 2 | 6 |  | 2
|  | Cylinder Lubricator Pump Motor # M-2101-LP A |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 0.4 |  | 1 | 0.4 |  | 1
|  | Cylinder Lubricator Oil Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 0.4 |  | 1 | 0.4 |  | 1
|  | Water Skid | Aux. Pump Motor # P-2101-AX A |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Main Pump Motor # P-2101-WP A |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Electric Heater # H-2101-WH A |  | 400 | Normal | 3Ph | — | 50 | — | Intermittent | 13.5 |  | 1 | 13.5 |  | 1
|  |  | Water Console Cooler Motor # AE-2101-WC A |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 3 |  | 2 | 6 |  | 2
2 | UCP Panel For Compressor # C-2101-C1 A # C-2102-C2 A | System control |  |  | 110 | UPS Redundant | 1Ph | — | 50 | — | Continuous | 1.5 |  | 1 | 1.5 |  | 2
|  | Socket & lighting |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1.5 |  | 1 | 1.5 |  | 1
3 | Compressor # C-2101-C1 B # C-2102-C2 B | Main Motor |  |  | 11000 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 1070 |  | 1 | 1070 |  | 1
|  | Space Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1 |  | 1 | 1 |  | 1
|  | Oil Heater # H-2101-LH B |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1.5 |  | 1 | 1.5 |  | 1
|  | Barring Device Motor # C-2101-BM B |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Intermittent | 2.2 |  | 1 | 2.2 |  | 1
|  | Electrical Heat Tracing (Part of HAVAYAR Scope ) |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 2 |  | 1 | 2 |  | 1
|  | Aux. Oil Pump Motor # M-2101-AP B |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 5.5 |  | 1 | 5.5 |  | 1
|  | Lube. Oil Cooler # AE-2101-OC B |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 3 |  | 2 | 6 |  | 2
|  | Cylinder Lubricator Pump Motor # M-2101-LP B |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 0.4 |  | 1 | 0.4 |  | 1
|  | Cylinder Lubricator Oil Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 0.4 |  | 1 | 0.4 |  | 1
|  | Water Skid | Aux. Pump Motor # P-2101-AX B |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Main Pump Motor # P-2101-WP B |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Electric Heater # H-2101-WH B |  | 400 | Normal | 3Ph | — | 50 | — | Intermittent | 13.5 |  | 1 | 13.5 |  | 1
|  |  | Water Console Cooler Motor # AE-2101-WC B |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Continuous | 3 |  | 2 | 6 |  | 2
4 | UCP Panel For Compressor # C-2101-C1 B # C-2102-C2 B | System control |  |  | 110 | UPS Redundant | 1Ph | — | 50 | — | Continuous | 1.5 |  | 1 | 1.5 |  | 2
|  | Socket & lighting |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1.5 |  | 1 | 1.5 |  | 1
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
ELECTRICAL/UPS CONSUMPTION LOAD LIST
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه 4 از 4
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | HY |  | 120 |  | EL | LI | 0001 | V01
5 | Compressor # C-2101-C1 C # C-2102-C2 C | Main Motor |  |  | 11000 | Normal | 3Ph | Yes | 50 | DOL | Standby | 1070 |  | 1 | 1070 |  | 1
|  | Space Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Standby | 1 |  | 1 | 1 |  | 1
|  | Oil Heater # H-2101-LH C |  |  | 230 | Normal | 1Ph | — | 50 | — | Standby | 1.5 |  | 1 | 1.5 |  | 1
|  | Barring Device Motor # C-2101-BM C |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 2.2 |  | 1 | 2.2 |  | 1
|  | Electrical Heat Tracing (Part of HAVAYAR Scope ) |  |  | 230 | Normal | 1Ph | — | 50 | — | Standby | 2 |  | 1 | 2 |  | 1
|  | Aux. Oil Pump Motor # M-2101-AP C |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 5.5 |  | 1 | 5.5 |  | 1
|  | Lube. Oil Cooler # AE-2101-OC C |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 3 |  | 2 | 6 |  | 2
|  | Cylinder Lubricator Pump Motor # M-2101-LP C |  |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 0.4 |  | 1 | 0.4 |  | 1
|  | Cylinder Lubricator Oil Heater |  |  | 230 | Normal | 1Ph | — | 50 | — | Standby | 0.4 |  | 1 | 0.4 |  | 1
|  | Water Skid | Aux. Pump Motor # P-2101-AX C |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Main Pump Motor # P-2101-WP C |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 5.5 |  | 1 | 5.5 |  | 1
|  |  | Electric Heater # H-2101-WH C |  | 400 | Normal | 3Ph | — | 50 | — | Standby | 13.5 |  | 1 | 13.5 |  | 1
|  |  | Water Console Cooler Motor # AE-2101-WC C |  | 400 | Normal | 3Ph | Yes | 50 | DOL | Standby | 3 |  | 2 | 6 |  | 2
6 | UCP Panel For Compressor # C-2101-C1 C # C-2102-C2 C | System control |  |  | 110 | UPS Redundant | 1Ph | — | 50 | — | Continuous | 1.5 |  | 1 | 1.5 |  | 2
|  | Socket & lighting |  |  | 230 | Normal | 1Ph | — | 50 | — | Intermittent | 1.5 |  | 1 | 1.5 |  | 1

## Messages (hidden)
Oval 931 | Sht 1
Oval 936 | Sht 1
Oval 1656 | Sht 1
Oval 87 | Sht 2
Oval 93 | Sht 2
Oval 94 | Sht 2
Oval 96 | Sht 2
Oval 502 | Sht 2
Oval 102 | Sht 2
Oval 89 | Sht 2
Oval 161 | Sht 4
Oval 525 | Sht 4
Oval 299 | Sht 4
Oval 209 | Sht 4
Rectangle 229 | Sht 4
Oval 241 | Sht 4
Oval 356 | Sht 5
Oval 349 | Sht 5
Oval 350 | Sht 5
Oval 581 | Sht 5
Oval 70 | Sht 11
Oval 71 | Sht 11
Oval 193 | Sht 12
Oval 192 | Sht 12
Oval 206 | Sht 12
Oval 196 | Sht 12
Oval 276 | Sht 13
Oval 277 | Sht 13
Oval 289 | Sht 13
Oval 321 | Sht 14
Oval 326 | Sht 14
Oval 546 | Sht 14
Oval 355 | Sht 14
Oval 358 | Sht 14
Oval 361 | Sht 14
Oval 369 | Sht 14
Oval 363 | Sht 14
Oval 371 | Sht 14
Oval 364 | Sht 14
Oval 372 | Sht 14