## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-EL-LI-0001
Document Title:ELECTRICAL/UPS CONSUMPTION LOAD LIST |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-HY-0006 |  |  | Transmital Date:1403/10/08
[5 empty] | NISOC Tr. No: NISOC- CRS-NISOC-BK-GCS-HY-120-EL-LI-0001_V00 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument comments :
1 |  |  | 02/2294/133777 | 1402/04/07 | 1- با توجه به مدرک PLC WIRING DIAGRAM & TERMINAL DETAILS با کد BK-GCS-HY-120-IN-DG-0001-Rev.00 مصرف UPS شامل power supply مدل 6EP1336-2BA10 است که مصرف ورودی اش 120*7.5=900 W است. مصارف UPS تنها شامل فن و power supply می باشد. مصارف Non-ups نیز با توجه به مدرک PLC WIRING DIAGRAM & TERMINAL DETAILS با کد BK-GCS-HY-120-IN-DG-0001-Rev.00 شامل روشنایی ها، هیترهاو سوکت است که در کل کمتر از 1.5 kw بر آورد شده است. 2- مقادیر قید شده در ستون Rated Power بر اساس Data sheetهای موتور می باشد که به صورت جداگانه در مدارک مختلف مقادیرشان خدمتتان ارائه شده است. محاسبات
Process comments :
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: 1403.07.07 |  |  |  |  | Date: