## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-EL-LI-0001_V00
Document Title: Electrical/UPS consumption Load List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0203-EL-TR-HY-0006-V00 |  |  | Transmital Date: 2024/10/08
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-EL-LI-0001_V00 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Electrical comments :
1 | No Comment. Note: If any chnages in vendor data, this document shall be updated and isuued again. |  | BK-SUR-ENG-MEC-02-08023 | 2023-07-02 | Noted.
Instrument comments :
| مصارف در نظر گرفته شده برای UCP-C به صورت Standby می باشد که مفهوم شفافی ندارد. این UCP در زمان راه اندازی کمپرسور سوم به صورت continuous در سرویس می باشد در حالی که دو کمپرسور دیگر نیز در سرویس هستند لذا مصارف آن باید به صورت کامل در نظر گرفته شود. |  | BK-SUR-ENG-MEC-02-08023 | 2023-07-02 | Noted.
| در خصوص مصارف non-UPS تمامی کمپرسورها امکان در نظر گرفته شدن آنها به صورت intermittent وجود دارد. |  | BK-SUR-ENG-MEC-02-08023 | 2023-07-02 | Noted.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 7/2/2023 |  |  |  |  | Date: