## Cover
NISOC |  |  |  | نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [8 empty] | شماره صفحه: 1 از 10
|  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  |  | BK | GCS | HY |  | 120 | IN | DS | 0002 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
DATASHEET FOR CONTROL/REGULATOR VALVES نگهداشت و افزایش تولید میدان نفتی بینک
V00 | OCT.2024 |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  |  |  | M.SADEGHIAN
Rev. | Date |  | Purpose of Issue/Status |  |  |  | Prepared By |  |  | Checked By |  |  |  | Approved By | Client Approval
Status:
IFA: Issued For Approval
IFR:Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## Index
نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [11 empty] | شماره صفحه: 2 از 10
[5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | HY | 120 | IN | DS |  | 0002 |  | V00
Tabulation Of Revised Pages
| Page | V00 | V01 | V02 |  | V03 |  | V04 |  |  | Page |  | V00 |  | V01 |  |  | V02 | V03 | V04
| 1 | X | [8 empty] | 36
| 2 | X | [8 empty] | 37
| 3 | X | [8 empty] | 38
| 4 | X | [8 empty] | 39
| 5 | X | [8 empty] | 40
| 6 | X | [8 empty] | 41
| 7 | X | [8 empty] | 42
| 8 | X | [8 empty] | 43
| 9 | X | [8 empty] | 44
| 10 | X | [8 empty] | 45
| 11 | [9 empty] | 46
| 12 | [9 empty] | 47
| 13 | [9 empty] | 48
| 14 | [9 empty] | 49
| 15 | [9 empty] | 50
| 16 | [9 empty] | 51
| 17 | [9 empty] | 52
| 18 | [9 empty] | 53
| 19 | [9 empty] | 54
| 20 | [9 empty] | 55
| 21 | [9 empty] | 56
| 22 | [9 empty] | 57
| 23 | [9 empty] | 58
| 24 | [9 empty] | 59
| 25 | [9 empty] | 60
| 26 | [9 empty] | 61
| 27 | [9 empty] | 62
| 28 | [9 empty] | 63
| 29 | [9 empty] | 64
| 30 | [9 empty] | 65
| 31 | [9 empty] | 66
| 32 | [9 empty] | 67
| 33 | [9 empty] | 68
| 34 | [9 empty] | 69
| 35 | [9 empty] | 70

## PRV
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:3از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | PRESSURE REGULATOR
| 2 | Tag Number |  |  | P&ID No. |  |  | PCV-2120A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001 page2/9
| 3 | Service |  |  | Pipe No. |  |  | Instrument Air |  |  |  | ISA-112-0002A-AZ00-2"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 1" |  |  |  | AZ00
| 5 | Pipe Material |  |  | Pipe Insulation |  |  | Galvanized Carbon steel |  |  |  | NP
Process Conditions | 6 | Fluid |  |  | State |  |  | Instrument Air |  |  |  | Gas
| 7 | Design Pressure bar(g) |  |  | Max. Shut-Off DP. bar(g) |  |  | 12.5 |  |  |  | 12.5
| 8 | Operating Temperature ℃ |  |  | Design Temperature ℃ |  |  | 65 |  |  |  | 85
| 9 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 9.155
| 10 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 2.3026 |  |  |  | 0.02108
| 11 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.417 |  |  |  | 0.9982
| 12 | Vapor Pressure |  |  | Critical Pressure (barg) | [6 empty] | 36.86
| 13 | Flow Rate |  |  |  |  | Unit | Min. Flow |  |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  |  | Nm3/h | 3 |  |  | 6 |  | 6
| 14 | Inlet Pressure |  |  |  |  | bar(g) | 6.01 |  |  | 7 |  | 8
| 15 | Outlet Pressure |  |  |  |  | bar(g) | 6 |  |  | 6 |  | 6
Calculation Data | 16 | Sizing Cv | [5 empty] | VTA
| 17 | Valve Travel |  |  |  |  | ％ |  |  |  | VTA
| 18 | Allowable SPL dBA |  |  | Predicated SPL dBA |  |  | <85 dB |  |  |  | N/A
| 19 | Rated Cv |  |  | Valve Fl |  |  | VTA |  |  |  | N/A
Valve Body/Bonnet | 20 | Model | [5 empty] | Self-operated
| 21 | Body Type |  |  | Control Mode |  |  | Globe |  |  |  | SELF
| 22 | Body Size |  |  | End Connection & Rating |  |  | 1" |  |  |  | Flange,300# RF
| 23 | Allowable Operating Temperature ℃ |  |  | Pressure Rating
| 24 | Bonnet Type |  |  | Flow Direction |  |  | Bolted |  |  |  | N/A
| 25 | Body Material |  |  | Stem/Shaft Material |  |  | Galvanized Carbon steel |  |  |  | S.S316L
Trim | 26 | Trim Type |  |  | Trim Size |  |  | Standard |  |  |  | Standard
| 27 | Trim Material |  |  | Seat Material |  |  | S.S316L |  |  |  | S.S316L
| 28 | Guiding |  |  | Packing Material |  |  | S.S316L |  |  |  | PTFE
| 29 | Characteristics |  |  | Seat Leakage Class |  |  | Linear |  |  |  | IV
Actuator | 30 | Model |  |  | Type |  |  | Diaphragm |  |  |  | Spring &Diaphragm
| 31 | Pilot |  |  | Restrictor Type |  |  | N/A |  |  |  | Internal
| 32 | Restrictor Input |  |  | Ext. Connection Size |  |  | DOWNSTREAM |  |  |  | -
| 33 | Seal Type |  |  | Spring Material |  |  | S.S316L |  |  |  | S.S316L
| 34 | Diaph. Temperature Rating |  |  | Diaph. Pressure Rating |  |  | 50 |  |  |  | 12
| 35 | Diaphragm Material |  |  | Available D. P. |  |  | EPDM · FKM · NBR
| 36 | Pressure Set Point | [5 empty] | 6 barg
| 37 | Temperature Assembly |  |  | Capillary Length |  |  | - |  |  |  | -
| 38 | Fail Position |  |  | Tubing&Fitting |  |  | Open |  |  |  | S.S316L
| 39 | Enclosure Protection | [5 empty] | IP65
Accessories | 40 | Filter |  |  | Mesh Size |  |  | - |  |  |  | -
| 41 | Condenser |  |  | Check Valve |  |  | - |  |  |  | -
| 42 | Inlet Gauge |  |  | Control Gauge |  |  | - |  |  |  | -
Miscell. | 43 | Manufacturer
| 44 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:4از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | PRESSURE REGULATOR
| 2 | Tag Number |  |  | P&ID No. |  |  | PCV-2205A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001-page:4
| 3 | Service |  |  | Pipe No. |  |  | N2 Gas Supply |  |  |  | NIT-112-0002A-SS-1"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 1" |  |  |  | S.S
| 5 | Pipe Material |  |  | Pipe Insulation |  |  | SS316L |  |  |  | NP
Process Conditions | 6 | Fluid |  |  | State |  |  | Nitrogen |  |  |  | Gas
| 7 | Design Pressure bar(g) |  |  | Max. Shut-Off DP. bar(g) |  |  | 12.5 |  |  |  | 12.5
| 8 | Operating Temperature ℃ |  |  | Design Temperature ℃ |  |  | 60 |  |  |  | 85
| 9 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 8.62
| 10 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 2.3188 |  |  |  | 0.019988
| 11 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.408 |  |  |  | 0.9989
| 12 | Vapor Pressure |  |  | Critical Pressure |  |  | NA |  |  |  | NA
| 13 | Flow Rate |  |  |  |  | Unit | Min. Flow |  |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  |  | Nm3/h | 0.3 |  |  | 3 |  | 3
| 14 | Inlet Pressure |  |  |  |  | Bar(g) | 4 |  |  | 7.5 |  | 8
| 15 | Outlet Pressure |  |  |  |  | Bar(g) | 0.5 |  |  | 0.5 |  | 0.5
Calculation Data | 16 | Sizing Cv
| 17 | Valve Travel |  |  |  |  | ％
| 18 | Allowable SPL dBA |  |  | Predicated SPL dBA |  |  | <85 dB |  |  |  | N/A
| 19 | Rated Cv |  |  | Valve Fl |  |  | VTA |  |  |  | N/A
Valve Body/Bonnet | 20 | Model | [5 empty] | Self-operated
| 21 | Body Type |  |  | Control Mode |  |  | Globe |  |  |  | SELF
| 22 | Body Size |  |  | End Connection & Rating |  |  | 1" |  |  |  | Flange,300# RF
| 23 | Allowable Operating Temperature ℃ |  |  | Pressure Rating
| 24 | Bonnet Type |  |  | Flow Direction |  |  | Bolted |  |  |  | N/A
| 25 | Body Material |  |  | Stem/Shaft Material |  |  | S.S316L |  |  |  | S.S316L
Trim | 26 | Trim Type |  |  | Trim Size |  |  | Standard |  |  |  | Standard
| 27 | Trim Material |  |  | Seat Material |  |  | S.S316L |  |  |  | S.S316L
| 28 | Guiding |  |  | Packing Material |  |  | S.S316L |  |  |  | PTFE
| 29 | Characteristics |  |  | Seat Leakage Class |  |  | Linear |  |  |  | IV
Actuator | 30 | Model |  |  | Type |  |  | Diaphragm |  |  |  | Spring&Diaphragm
| 31 | Pilot |  |  | Restrictor Type |  |  | N/A |  |  |  | Internal
| 32 | Restrictor Input |  |  | Ext. Connection Size |  |  | DOWNSTREAM |  |  |  | -
| 33 | Seal Type |  |  | Spring Material |  |  | S.S316L |  |  |  | S.S316L
| 34 | Diaph. Temperature Rating |  |  | Diaph. Pressure Rating |  |  | 65 |  |  |  | 12
| 35 | Diaphragm Material |  |  | Available D. P. |  |  | EPDM · FKM · NBR
| 36 | Pressure Set Point | [5 empty] | 1 Barg
| 37 | Temperature Assembly |  |  | Capillary Length |  |  | - |  |  |  | -
| 38 | Fail Position |  |  | Tubing&Fitting |  |  | Open |  |  |  | S.S316L
| 39 | Enclosure Protection | [5 empty] | _
Accessories | 40 | Filter |  |  | Mesh Size |  |  | - |  |  |  | -
| 41 | Condenser |  |  | Check Valve |  |  | - |  |  |  | -
| 42 | Inlet Gauge |  |  | Control Gauge |  |  | - |  |  |  | -
Miscell. | 43 | Manufacturer
| 44 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:5از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | PRESSURE REGULATOR
| 2 | Tag Number |  |  | P&ID No. |  |  | PCV-2206A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001-page:4
| 3 | Service |  |  | Pipe No. |  |  | N2 Gas Supply |  |  |  | NIT-112-0001A-SS-1"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 1" |  |  |  | S.S
| 5 | Pipe Material |  |  | Pipe Insulation |  |  | SS316L |  |  |  | NP
Process Conditions | 6 | Fluid |  |  | State |  |  | Nitrogen |  |  |  | Gas
| 7 | Design Pressure bar(g) |  |  | Max. Shut-Off DP. bar(g) |  |  | 12.5 |  |  |  | 12.5
| 8 | Operating Temperature ℃ |  |  | Design Temperature ℃ |  |  | 60 |  |  |  | 85
| 9 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 8.62
| 10 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 2.3188 |  |  |  | 0.019988
| 11 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.408 |  |  |  | 0.9989
| 12 | Vapor Pressure |  |  | Critical Pressure |  |  | NA |  |  |  | NA
| 13 | Flow Rate |  |  |  |  | Unit | Min. Flow |  |  | Nor. Flow |  | Max. Flow
|  | kg/h(Liquid,Steam),Nm3/h(Gas) |  |  |  |  | Nm3/h | 0.3 |  |  | 3 |  | 3
| 14 | Inlet Pressure |  |  |  |  | Bar(g) | 4 |  |  | 7.5 |  | 8
| 15 | Outlet Pressure |  |  |  |  | Bar(g) | 2 |  |  | 2 |  | 2
Calculation Data | 16 | Sizing Cv
| 17 | Valve Travel |  |  |  |  | ％
| 18 | Allowable SPL dBA |  |  | Predicated SPL dBA |  |  | <85 dB |  |  |  | N/A
| 19 | Rated Cv |  |  | Valve Fl |  |  | VTA |  |  |  | N/A
Valve Body/Bonnet | 20 | Model | [5 empty] | Self-operated
| 21 | Body Type |  |  | Control Mode |  |  | Globe |  |  |  | SELF
| 22 | Body Size |  |  | End Connection & Rating |  |  | 1" |  |  |  | Flange,300# RF
| 23 | Allowable Operating Temperature ℃ |  |  | Pressure Rating
| 24 | Bonnet Type |  |  | Flow Direction |  |  | Bolted |  |  |  | N/A
| 25 | Body Material |  |  | Stem/Shaft Material |  |  | S.S316L |  |  |  | S.S316L
Trim | 26 | Trim Type |  |  | Trim Size |  |  | Standard |  |  |  | Standard
| 27 | Trim Material |  |  | Seat Material |  |  | S.S316L |  |  |  | S.S316L
| 28 | Guiding |  |  | Packing Material |  |  | S.S316L |  |  |  | PTFE
| 29 | Characteristics |  |  | Seat Leakage Class |  |  | Linear |  |  |  | IV
Actuator | 30 | Model |  |  | Type |  |  | Diaphragm |  |  |  | Spring&Diaphragm
| 31 | Pilot |  |  | Restrictor Type |  |  | N/A |  |  |  | Internal
| 32 | Restrictor Input |  |  | Ext. Connection Size |  |  | Downstream |  |  |  | -
| 33 | Seal Type |  |  | Spring Material |  |  | S.S316L |  |  |  | S.S316L
| 34 | Diaph. Temperature Rating |  |  | Diaph. Pressure Rating |  |  | 65 |  |  |  | 12
| 35 | Diaphragm Material |  |  | Available D. P. |  |  | EPDM · FKM · NBR
| 36 | Pressure Set Point | [5 empty] | 2.2 Barg
| 37 | Temperature Assembly |  |  | Capillary Length |  |  | - |  |  |  | -
| 38 | Fail Position |  |  | Tubing&Fitting |  |  | Open |  |  |  | S.S316L
| 39 | Enclosure Protection | [5 empty] | _
Accessories | 40 | Filter |  |  | Mesh Size |  |  | - |  |  |  | -
| 41 | Condenser |  |  | Check Valve |  |  | - |  |  |  | -
| 42 | Inlet Gauge |  |  | Control Gauge |  |  | - |  |  |  | -
Miscell. | 43 | Manufacturer
| 44 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## PCV
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
DATASHEET FOR CONTROL/REGULATOR VALVES
Contract No: |  |  | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence |  | Rev | شماره صفحه:6از10
053-073-9184 |  |  | BK | GCS | HY | 120 | IN | DS | 0002 |  | V00
TAG NO. :PCV-2123A/B/C |  |  |  | Line Num: GAS-111-0045A-FS00-6"-IS |  |  |  | P&ID NO. : | BK-GSC-HY-120-PR-PI-001-Rev.01 Page 1 /3
1 | SERVICE CONDITIONS | FLUID : |  | Hydrocarbon
[5 empty] | UNITS | 25% Summer |  | 25% Winter |  |  |  | Summer | Winter
2 |  | STATE |  |  |  | Two Phase (Note 1) |  | Gas (Note 1) |  |  |  | Two Phase (Note 1) | Gas (Note 1)
3 |  | GAS MASS FLOW RATE (Liq. / Gas) |  |  | Kg/hr | 10 / 2223 |  | 2086 |  |  |  | 38.54 / 8897 | 8343.5
4 |  | INLET PRESSURE |  |  | barg | 54.1 |  | 54.1 |  |  |  | 54.1 | 54.1
5 |  | PRESSURE DIFFERENTIAL |  |  | bar | 49 |  | 49 |  |  |  | 49 | 49
6 |  | INLET TEMPERATURE |  |  | °C | 60 |  | 60 |  |  |  | 60 | 60
7 |  | MOLECULAR WEIGHT (Liq. / Gas) |  |  | M | 18.05 / 24.56 |  | - / 21.56 |  |  |  | 18.05 / 24.56 | - / 21.56
8 |  | DYNAMIC VISCOSITY (Liq. / Gas) |  |  | cP | 0.4943 / 0.0142 |  | - / 0.0139 |  |  |  | 0.4943 / 0.0142 | - / 0.0139
9 |  | RATIO OF SPECIFIC HEATS (Liq. / Gas) |  |  |  | 1.163 / 1.462 |  | 1.434 |  |  |  | 1.163 / 1.462 | 1.434
10 |  | INLET COMPRESSIBILITY FACTOR |  |  |  | 0.0366 / 0.8229 |  | 0.868 |  |  |  | 0.0366 / 0.8229 | 0.868
11 |  | *REQUIRED CV |  |  |  | VTS |  | VTS |  |  |  | VTS | VTS
12 |  | *TRAVEL |  |  | % | VTS |  | VTS |  |  |  | VTS | VTS
13 |  | ALLOWABLE/*PREDICTED SPL |  |  | dBA | < 85 |  | < 85 |  |  |  | < 85 | VTS
14 | LINE | PIPE LINE SIZE |  | 6" |  | 46 | ACTUATOR | *TYPE | Spring Diaphragm
15 | [5 empty] | 47 |  | *MFR & MODEL | VTS
16 |  | PIPE LINE Mat. / INSULATION |  | Stainless Steel / No Insulation |  | 48 |  | *SIZE VTS EFF. AREA |  |  |  | VTS
17 | VALVE BODY/BONNET | *TYPE |  | Globe Valve |  | 49 |  | ON/OFF MODULATING: YES
18 |  | *SIZE /RATING |  | VTA , #600, Line Sch:40S |  | 50 |  | SPRING ACTION OPEN/CLOSE |  |  |  | AIR TO OPEN
19 |  | DESIGN PRESS/TEMP. |  | 62 barg /180 °C |  | 51 |  | *MAX. ALLOWABLE PRESSURE VTS |  |  | 10barg
20 |  | *MFR & MODEL |  |  |  | 52 |  | *MIN REQUIRED PRESSURE VTS |  |  | 4 barg
21 |  | *BODY/BONNET MATL |  | ASTM A351 CF3M( NACE MR0175) |  | 53 |  | AVAILABLE AIR SUPPLY PRESSURE (barg) |  |  |  |  | 4 barg
22 |  | *LINER MATERIAL/ID |  | S.S316 ( NACE MR0175) |  | 54 |  | MAX:10 barg MIN: 4 barg
23 |  | END CONNECTION |  | Flanged |  | 55 |  | *BENCH RANGE |  |  |  | -
|  | FLG. FACE FINISH |  | Raised Face |  | 56 |  | ACT ORIENTATION Vertical |  | Horizontal
24 |  | END EXT/MATL |  |  |  | 57 |  | HANDWHEEL TYPE |  |  |  | N/A
25 |  | *FLOW DIRECTION |  |  |  | 58 |  | AIR FAILURE VALVE: Yes,Open SET AT |  |  |  |  | -
26 |  | *TYPE OF BONNET |  | Bolted Bonnet |  | 59 | POSITIONER | INPUT SIGNAL |  |  | 4-20 mA
27 |  | LUB & ISO VALVE |  |  |  | 60 |  | *TYPE: Smart HART
28 |  | *PACKING MATERIAL |  | Teflon-Chevron |  | 61 |  | *MFR & MODEL | VTS |  | AIR CONN.: 1/4" NPTF
29 |  | *PACKING TYPE |  |  |  | 62 |  | *ON INCR SIGNAL OUTPUT INCR/DECR: |  |  |  | VALVE CLOSE ON INCREASE SIGNAL OUTPUT
30 | TRIM | *TYPE |  | Trim No. 10 |  | 63 |  | GAUGES: YES BYPASS |  |  |  |  | YES
31 |  | *SIZE |  | *RATED TRAVEL |  | 64 |  | MATERIAL | Aluminum
32 |  | *CHARACTRISTIC |  | VTA |  | 65 |  | ENCLOSURE CLASS |  |  |  | EX ia , IIB, T4
33 |  | *BALANCED / UNBALANCED |  | VTA |  | 66 |  | INGRESS PROTECTION |  |  |  | IP 66
34 |  | DIAPHRAGM MATERIAL |  | VTA |  | 67 | POSITION FEEDBACK TRANS. | OUTPUT | 4-20 mA EX ia , IIB, T4 |  |  | TAG NO.
35 |  | PLUG/BALL/DISK MATERIAL |  | Trim No. 10 |  | 68 |  | AUXILIARY POWER |  |  |  | 24 VDC
36 |  | SEAT MATERIAL |  | Trim No. 10 ( NACE MR0175) |  | 69 |  | HOUSING MATERIAL |  |  |  | Included in Positioner
37 |  | GUIDE MATERIAL |  | Trim No. 10 ( NACE MR0175) |  | 70 |  | INGRESS PROTECTION |  |  |  | IP66
38 |  | STEM MATERIAL |  | Trim No. 10 ( NACE MR0175) |  | 71 | AIR SET | *MFR & MODEL VTS AIR CONN.: 1/4" NPTF
38 |  | CAGE MATERIAL |  | Trim No. 10 ( NACE MR0175) |  | 71
39 |  | GASKET MATERIAL |  | Spiral Wound, 4.45 mm Thick., RF, SF, S.S 316 Winding/ Graphite Filler, C.S. Outer& S.S 316L Inner Ring ASME B16.20 |  | 72 |  | *SET PRESSURE |  |  | 4 barg
40 | [5 empty] | 73 |  | FILTER: Yes GAUGE: Yes
41 | ACCESSORIES | SOLENOID VALVE: | YES, Body S.S316 |  |  | 74 | TEST | *HYDRO PRESSURE |  |  |  | Yes
42 |  | COIL RATING: | Class F |  |  | 75 |  | ANSI/FCI LEAKAGE CLASS: |  |  |  | IV
43 |  | SUPPLY VOLTAGE | 24VDC |  |  | 76
44 |  | INGRESS PROTECTION | IP66 , EXd IIB T4
45 |  | Limit Switch (Open/Close) | Limit switch box Body Aluminum-24vdc-IP66 , EXd IIB T4
NOTES:
1- See gas composition in attachment.
2- M20 x 1.5 Cable gland shall be provided by vendor.
3- VTS: Vendor to Specifiy, VTC: Vendor to Confirm, N/A: Not Applicable
4- Trim number shall be confirmed by Vendor.
5-LEAKAGE CLASS IV
* All information shall be confirmed by Vendor.

## PCV (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
DATASHEET FOR CONTROL/REGULATOR VALVES
Contract No: | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence | Rev | شماره صفحه:7از10
053-073-9184 | BK | GCS | HY | 120 | IN | DS | 0002 | V00

## TCV Water
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:8از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | Temperature Control Valve
| 2 | Tag Number |  |  | P&ID No. |  |  | TCV-2220 A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001-page 5
| 3 | Service |  |  | Pipe No. |  |  | Water Skid |  |  |  | CWS-112-0001A-C.S-3"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 3" |  |  |  | C.S
| 5 | Pipe Material |  |  | Pipe Insulation | [6 empty] | NP
Process Conditions | 6 | Fluid |  |  | State |  |  | Water + Glycol |  |  |  | Liquid
| 7 | Design Pressure bar(g) |  |  | Design Temperature °C |  |  | 8 |  |  |  | 85
| 8 | Operating Pressure bar(g) |  |  | Operating Temperature ℃ |  |  | 4 |  |  |  | 50 ~ 70
| 9 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 1076~1060
| 10 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 2.761 ~ 1.766 |  |  |  | 2.971 ~ 1.872
| 11 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.098 ~ 1.1 |  |  |  | 0.00675 ~ 0.00646
| 12 | Vapor Pressure |  |  | Critical Pressure |  |  | NA |  |  |  | NA
| 13 | Flow Rate |  |  |  |  | Unit | Cold Inlet Stream |  |  | Hot Inlet Stream |  | Outlet Stream
|  | Liquid Flow Rate |  |  |  |  | kg/h | 0 ~ 15300 |  |  | 0 ~ 15300 |  | 15300
| 14 | Working temperature |  |  |  |  | °C | 50 ~ 63 |  |  | 63 ~ 70 |  | 63
| 15 | Outlet Pressure |  |  |  |  | Bar(g) | [5 empty] | VTS
| 16 | Temperature Set Point | [5 empty] | 63
| 17 | Allowable SPL dBA | [5 empty] | <85 dB
| 18 | Area Clasification | [5 empty] | Zone2,IIB,T4
Valve Characteristics | 19 | Model | [5 empty] | Self-operated
| 20 | Type | [5 empty] | Three-way Thermostatic Control Valve
| 21 | Body Size |  |  | End Connection & Rating |  |  | 3" |  |  |  | Flange,300# RF
| 22 | Body Material | [5 empty] | A216 GR. WCB
| 23 | Trim Material | [5 empty] | Trim No.12
| 24 | Seat Leakage Class | [5 empty] | IV
| 25 | Restrictor Input | [5 empty] | DOWNSTREAM
| 26 | Seal Type | [5 empty] | VTA
| 27 | Rated Cv
| 28 | Fail Position | [5 empty] | Open
| 29 | Weight
Accessories | 30 | Accessories
Miscell. | 31 | Manufacturer
| 32 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument . 2- The control valve has the function of controlling the excess discharge pressure of pump. The control valve will be openned if the pressure be higher than 6 barg.

## TCV OIL
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:9از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | Temperature Control Valve
| 2 | Tag Number |  |  | P&ID No. |  |  | TCV-2204 A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001-page 3
| 3 | Service |  |  | Pipe No. |  |  | Oil Skid |  |  |  | OIL-112-0015A-S.S-2"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 2" |  |  |  | S.S
| 5 | Pipe Material |  |  | Pipe Insulation | [6 empty] | NP
Process Conditions | 6 | Fluid |  |  | State |  |  | Mineral Oil ISO VG 100 (Liquid, SG: 0.88, Viscosity: 100 cP) |  |  |  | Liquid
| 7 | Design Pressure bar(g) |  |  | Design Temperature °C |  |  | 10 |  |  |  | 85
| 8 | Operating Pressure bar(g) |  |  | Operating Temperature ℃ |  |  | 5 |  |  |  | 5 ~ 70
| 9 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 869
| 10 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 33.855 |  |  |  | 29.42
| 11 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.148 |  |  |  | 0.06216
| 12 | Vapor Pressure |  |  | Critical Pressure |  |  | NA |  |  |  | 15.86
| 13 | Flow Rate |  |  |  |  | Unit | Cold Inlet Stream |  |  | Hot Inlet Stream |  | Outlet Stream
|  | Liquid Flow Rate |  |  |  |  | lit/min | 0 ~ 131 |  |  | 0 ~ 131 |  | 131
| 14 | Working temperature |  |  |  |  | °C | 5 ~ 60 |  |  | 60 ~ 70 |  | 60
| 15 | Outlet Pressure |  |  |  |  | Bar(g) | [5 empty] | VTS
| 16 | Temperature Set Point | [5 empty] | 60 °C
| 17 | Allowable SPL dBA | [5 empty] | <85 dB
| 18 | Area Clasification | [5 empty] | Zone2,IIB,T4
Valve Characteristics | 19 | Model | [5 empty] | Self-operated
| 20 | Type | [5 empty] | Three-way Thermostatic Control Valve
| 21 | Body Size |  |  | End Connection & Rating |  |  | 2" |  |  |  | Flange,300# RF
| 22 | Body Material | [5 empty] | ASTM A182 GR.F316L
| 23 | Trim Material | [5 empty] | ,Trim No.10
| 24 | Seat Leakage Class | [5 empty] | IV
| 25 | Restrictor Input | [5 empty] | DOWNSTREAM
| 26 | Seal Type | [5 empty] | VTA
| 27 | Rated Cv
| 28 | Fail Position | [5 empty] | Open
| 29 | Weight
Accessories | 30 | Accessories
Miscell. | 31 | Manufacturer
| 32 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .

## PCV OIL
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پيمان: 053-073-9184 |  |  | DATASHEET FOR CONTROL/REGULATOR VALVES | [7 empty] | شماره صفحه:10از10
|  |  | BK | GCS | HY | 120 | IN | DS | 0002 | V00
General | 1 | Instrument Name | [5 empty] | PRESSURE REGULATOR
| 2 | Tag Number |  |  | P&ID No. |  |  | PCV-2201 A/B/C |  |  |  | BK-GCS-HY-120-PR-PI-0001-page 3
| 3 | Service |  |  | Pipe No. |  |  | Oil Skid |  |  |  | OIL-112-0007A-S.S-2"-IS
| 4 | Pipe O. D. /I. D. mm |  |  | Pipe Class |  |  | 2" |  |  |  | S.S
| 5 | Pipe Material |  |  | Pipe Insulation | [6 empty] | NP
| 6 | Area Clasification | [5 empty] | Zone2,IIB,T4
Process Conditions | 7 | Fluid |  |  | State |  |  | Mineral Oil ISO VG 100 (Liquid, SG: 0.88, Viscosity: 100 cP) |  |  |  | Liquid
| 8 | Design Pressure bar(g) |  |  | Max. Shut-Off DP. bar(g) |  |  | 10
| 9 | Operating Temperature ℃ |  |  | Design Temperature ℃ |  |  | 5 ~ 70 |  |  |  | 85
| 10 | Operating Density kg/m3 |  |  | Standard Density kg/Nm3 |  |  | 862
| 11 | Kinetic Viscosity (mm2/S) |  |  | Dynamic Viscosity (cP) |  |  | 22.4478 |  |  |  | 19.35
| 12 | Speci. Heat Ratio Cp/Cv |  |  | Compress Factor |  |  | 1.15 |  |  |  | 0.0608
| 13 | Vapor Pressure |  |  | Critical Pressure (bar) | [6 empty] | 15.86
| 14 | Flow Rate |  |  |  |  | Unit | Min. Flow |  |  | Nor. Flow |  | Max. Flow
|  | Liquid Flow Rate |  |  |  |  | lit/min | 13 |  |  | 20 |  | 131
| 15 | Inlet Pressure |  |  |  |  | bar(g) | 6 |  |  | 6 (Note 2) |  | 6
| 16 | Outlet Pressure |  |  |  |  | bar(g) | Amb |  |  | Amb |  | Amb
Calculation Data | 17 | Sizing Cv | [5 empty] | VTA
| 18 | Valve Travel |  |  |  |  | ％ |  |  |  | VTA
| 19 | Allowable SPL dBA |  |  | Predicated SPL dBA |  |  | <85 dB |  |  |  | N/A
| 20 | Rated Cv |  |  | Valve Fl |  |  | VTA |  |  |  | N/A
Valve Body/Bonnet | 21 | Model | [5 empty] | Self-operated
| 22 | Body Type |  |  | Control Mode |  |  | Globe |  |  |  | SELF
| 23 | Body Size |  |  | End Connection & Rating |  |  | 2"
| 25 | Bonnet Type |  |  | Flow Direction |  |  | Bolted |  |  |  | N/A
| 26 | Body Material |  |  | Stem/Shaft Material |  |  | ASTM A182 GR.F316L |  |  |  | Trim No.10
Trim | 27 | Trim Type |  |  | Trim Size |  |  | Standard |  |  |  | Standard
| 28 | Trim Material |  |  | Seat Material |  |  | Trim No.10 |  |  |  | Trim No.10
| 29 | Guiding |  |  | Packing Material |  |  | S.S316L |  |  |  | PTFE
| 30 | Characteristics |  |  | Seat Leakage Class |  |  | Linear |  |  |  | IV
Actuator | 31 | Model |  |  | Type |  |  | Diaphragm |  |  |  | Spring &Diaphragm
| 32 | Pilot |  |  | Restrictor Type |  |  | N/A |  |  |  | Internal
| 33 | Restrictor Input |  |  | Ext. Connection Size |  |  | DOWNSTREAM |  |  |  | -
| 34 | Seal Type |  |  | Spring Material |  |  | S.S316L |  |  |  | S.S316L
| 35 | Diaph. Temperature Rating |  |  | Diaph. Pressure Rating |  |  | 50 |  |  |  | 12
| 36 | Diaphragm Material |  |  | Available D. P. |  |  | VTA
| 37 | Pressure Set Point | [5 empty] | 6 barg
| 38 | Temperature Assembly |  |  | Capillary Length |  |  | - |  |  |  | -
| 39 | Fail Position |  |  | Tubing&Fitting |  |  | Open |  |  |  | S.S316L
| 40 | Enclosure Protection | [5 empty] | IP65
Accessories | 41 | Filter |  |  | Mesh Size |  |  | - |  |  |  | -
| 42 | Condenser |  |  | Check Valve |  |  | - |  |  |  | -
| 43 | Inlet Gauge |  |  | Control Gauge |  |  | - |  |  |  | -
Miscell. | 44 | Manufacturer
| 45 | Requisition No.
NOTES：
1- Each Instrument Shall Have a S.S. Tag Plate With Purchaser's Tag Number, The Tag Plate Shall Be Permanently Attached To The Instrument .